## LCWT 40F
ACSC Performance Data (English System, 50Hz) — Leaving Chilled Water Temp 40°F
UNIT SIZE | 95°F AMBIENT |  |  |  |  | 105°F AMBIENT |  |  |  |  | 115°F AMBIENT |  |  |  |  | 118.4°F AMBIENT |  |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg)
ACSC080 | 75.1 | 81.8 | 9.9 | 180.4 | 14.1 | 69 | 91.7 | 8.2 | 165.6 | 12 | 62.5 | 102.7 | 6.7 | 149.5 | 9.7 | 59.8 | 106.7 | 6.2 | 143.5 | 9.2 | 55.1 | 118.5 | 5.3 | 132.2 | 7.9
ACSC090 | 83.8 | 99.8 | 9.2 | 201.2 | 17.6 | 76.4 | 111.8 | 7.6 | 183.4 | 15 | 68.4 | 125.1 | 6.1 | 164.1 | 11.8 | 65.5 | 129.9 | 5.6 | 152.1 | 10.9 | 59.9 | 139.6 | 4.8 | 143.8 | 9.2
ACSC100 | 96.9 | 105.3 | 9.9 | 232.6 | 23.3 | 91.1 | 122.6 | 8.1 | 218.7 | 20.8 | 84.4 | 141.5 | 6.6 | 202.7 | 17.8 | 81.9 | 148.2 | 6.1 | 196.6 | 16.6 | 76.8 | 160.9 | 5.3 | 184.3 | 14.8
ACSC110 | 103.3 | 111.6 | 10 | 247.9 | 12.5 | 94.6 | 125 | 8.3 | 221.2 | 10.6 | 85.2 | 140 | 6.7 | 204.4 | 8.5 | 81.8 | 145.5 | 6.2 | 196.3 | 7.9 | 75.2 | 156.4 | 5.3 | 180.4 | 6.9
ACSC120 | 113.6 | 128.9 | 9.6 | 272.6 | 15 | 106.5 | 149.9 | 7.9 | 255.7 | 13.2 | 98.2 | 172.6 | 6.4 | 235.7 | 11.1 | 95 | 180.5 | 5.9 | 228 | 10.4 | 88.7 | 195.6 | 5.1 | 213 | 9.2
ACSC130 | 122 | 144.4 | 9.4 | 293 | 20.8 | 116.4 | 167.5 | 7.6 | 285.1 | 18.9 | 105 | 192.4 | 6.3 | 252 | 12.7 | 101.5 | 201.2 | 5.7 | 243.7 | 12.2 | 94.3 | 217.9 | 4.9 | 229.4 | 10.6
ACSC140 | 130.4 | 133 | 10.5 | 312.9 | 22.6 | 122.9 | 155 | 8.6 | 295 | 20.3 | 114.9 | 179.4 | 7 | 274 | 17.3 | 110.6 | 186 | 6.4 | 266 | 16.4 | 105.1 | 201 | 5.4 | 249.9 | 14.6
ACSC160 | 152.9 | 182.2 | 9.8 | 366.9 | 30.7 | 142.7 | 211.4 | 7.5 | 342.4 | 27 | 130.9 | 242.7 | 6.1 | 314.1 | 22.9 | 126.4 | 253.6 | 5.6 | 303.3 | 21.3 | 117.5 | 274.3 | 4.9 | 281.9 | 18.5
ACSC180 | 169.6 | 189.2 | 9.8 | 407 | 12.7 | 159.2 | 220.2 | 8 | 382.1 | 11.1 | 146.9 | 253.8 | 6.5 | 352.7 | 9.7 | 142.4 | 265.6 | 6 | 341.7 | 9 | 132.9 | 288.1 | 5.2 | 319 | 7.9
ACSC190 | 181.5 | 210.6 | 9.5 | 435.7 | 14.9 | 169.7 | 244.3 | 7.7 | 407.2 | 12.7 | 155.9 | 280.8 | 6.2 | 374.1 | 10.6 | 150.6 | 293.5 | 5.8 | 361.5 | 10.2 | 140.2 | 317.9 | 5 | 336.4 | 8.8
ACSC200 | 186.9 | 203.7 | 10.1 | 448.6 | 13.2 | 175.6 | 236.8 | 8.2 | 421.4 | 11.6 | 162.2 | 272.9 | 6.7 | 389.3 | 10 | 157 | 285.5 | 6.2 | 376.8 | 9.5 | 146.9 | 310.1 | 5.4 | 352.5 | 8.5
ACSC210 | 196.2 | 214.3 | 10.1 | 470.9 | 14.6 | 184 | 249 | 8.2 | 441.2 | 12.7 | 170 | 287 | 6.6 | 407.7 | 11.1 | 164.1 | 300.4 | 6.1 | 394 | 10.4 | 152.5 | 326 | 5.3 | 366.1 | 9
ACSC220 | 207.5 | 239.4 | 9.4 | 498.1 | 14.3 | 194 | 277.7 | 7.8 | 465.7 | 12.5 | 178.7 | 319.1 | 6.3 | 428.6 | 10.4 | 172.3 | 333.6 | 5.8 | 413.5 | 9.9 | 160.2 | 361.3 | 5.1 | 384.5 | 8.5
ACSC240 | 224 | 248.1 | 10 | 537.6 | 16.5 | 210 | 288.2 | 8.1 | 504.1 | 14.7 | 193.6 | 332 | 6.6 | 464.7 | 12.5 | 187.2 | 347.5 | 6.1 | 450.4 | 11.7 | 175.2 | 372.2 | 5.3 | 420.5 | 10.5
ACSC250 | 235.1 | 272.3 | 9.6 | 564.2 | 18.2 | 220 | 316.1 | 7.8 | 528 | 15.9 | 202 | 363.3 | 6.4 | 484.8 | 13.5 | 195.5 | 390.6 | 5.7 | 469.1 | 12.7 | 181.3 | 411.1 | 5 | 435.1 | 10.9
ACSC260 | 244 | 290.1 | 9.4 | 585.6 | 19.5 | 227.6 | 336.2 | 7.6 | 546.3 | 17.1 | 208.4 | 385.8 | 6.1 | 500.2 | 14.6 | 201.1 | 403 | 5.7 | 482.6 | 13.5 | 186.7 | 436.2 | 4.9 | 448.1 | 11.6
ACSC270 | 252.8 | 274.6 | 10.1 | 606.7 | 14.3 | 237.3 | 319.1 | 8.3 | 569.5 | 12.7 | 219 | 367.9 | 6.7 | 525.6 | 10.7 | 212.1 | 385.7 | 6.1 | 509.1 | 10 | 198.1 | 418.5 | 5.4 | 475.5 | 8.9
ACSC280 | 265 | 291 | 10 | 636 | 15.7 | 240.7 | 337.8 | 8.1 | 590.5 | 13.9 | 226.3 | 389 | 6.6 | 543.2 | 11.5 | 219.1 | 407.1 | 6.1 | 525.7 | 10.6 | 204.4 | 441.9 | 5.2 | 485.8 | 9
ACSC300 | 280.2 | 305.8 | 10.1 | 672.4 | 11.6 | 256.1 | 341.8 | 8.3 | 614.5 | 9.7 | 230.1 | 382.1 | 6.7 | 552.2 | 8.1 | 220.7 | 396.6 | 6.2 | 529.6 | 7.4 | 202.4 | 425.5 | 5.4 | 485.8 | 6.2
ACSC310 | 289 | 325.1 | 9.8 | 693.7 | 12.4 | 263.5 | 363.1 | 8.1 | 632.3 | 10.2 | 236.4 | 405.8 | 6.5 | 567.4 | 8.4 | 226.5 | 421.1 | 6.1 | 543.6 | 7.7 | 207.5 | 451.7 | 5.2 | 497.9 | 6.5
ACSC320 | 297.9 | 344.4 | 9.6 | 714.9 | 12.9 | 271.1 | 384.6 | 7.9 | 650.6 | 10.6 | 242.7 | 429.5 | 6.4 | 582.5 | 8.7 | 232.3 | 445.6 | 5.9 | 557.6 | 8 | 212.4 | 477.7 | 5 | 508.8 | 6.9
ACSC330 | 308.9 | 358.1 | 9.6 | 741.3 | 13.6 | 288.6 | 415.3 | 7.8 | 692.8 | 12.2 | 265 | 477 | 6.3 | 635.9 | 10.4 | 256.1 | 498.7 | 5.8 | 614.7 | 9.7 | 238.3 | 540.1 | 5 | 571.9 | 8.3
ACSC350 | 325.7 | 372.4 | 9.7 | 781.8 | 12.2 | 297.1 | 416.1 | 8 | 712.7 | 10.6 | 265.8 | 464.6 | 6.4 | 638 | 8.7 | 254.9 | 482.2 | 6 | 611.7 | 7.6 | 233.2 | 517.1 | 5.1 | 559.5 | 7.2
ACSC365 | 343.7 | 397.9 | 9.6 | 825.1 | 13.6 | 318.3 | 455.3 | 7.6 | 763.9 | 13 | 285.7 | 485.6 | 6.6 | 738 | 18.2 | 274.2 | 540 | 6.4 | 718 | 17.3 | 242.1 | 608.8 | 5.2 | 667.6 | 15.2
ACSC380 | 356.7 | 401.8 | 9.8 | 856 | 14.3 | 334.4 | 466.8 | 8 | 802.6 | 11.9 | 297.7 | 533.7 | 6.3 | 738 | 18.2 | 298.2 | 561.7 | 6 | 715.7 | 17.3 | 277 | 608.8 | 5.2 | 667.6 | 15.2
ACSC400 | 377 | 435.4 | 9.6 | 904.9 | 26.8 | 352.6 | 504.9 | 7.8 | 846.2 | 23.5 | 325.7 | 609.5 | 6 | 776.8 | 20.1 | 312.6 | 606.3 | 5.9 | 750.3 | 19.2 | 290.9 | 656.9 | 5.1 | 698.2 | 16.2
ACSC420 | 393.4 | 415.3 | 9.7 | 944.2 | 23.5 | 357.9 | 498.1 | 8 | 881.7 | 22.9 | 336.8 | 601.6 | 6.4 | 808.4 | 19.2 | 325.3 | 628.7 | 5.9 | 780.8 | 17.8 | 302.3 | 681.3 | 5.1 | 725.4 | 15.9
ACSC450 | 425.6 | 447.8 | 10.4 | 1021.4 | 29.6 | 400.2 | 520.9 | 8.5 | 960.5 | 26.8 | 370.5 | 601.5 | 6.9 | 889.3 | 22.6 | 359.6 | 630.3 | 6 | 863.1 | 21.3 | 336.7 | 685.4 | 5.5 | 808.1 | 18.6
ACSC475 | 447.8 | 496.2 | 10 | 1075 | 33 | 419.9 | 576.4 | 8.1 | 1007.7 | 29.3 | 387.2 | 664 | 6.6 | 929.1 | 24.9 | 375.1 | 694.9 | 6 | 900.2 | 23.3 | 350.1 | 752.2 | 5.3 | 840.2 | 20.6
ACSC500 | 470.3 | 544.6 | 9.4 | 1128.7 | 36.5 | 439.6 | 632 | 7.6 | 1055.2 | 31.9 | 405.9 | 726.5 | 6.3 | 973.6 | 27 | 390.6 | 750.6 | 6 | 937.6 | 25.5 | 365.4 | 805.2 | 5.4 | 873.5 | 23.1

## LCWT 42F
ACSC Performance Data (English System, 50Hz) — Leaving Chilled Water Temp 42°F
UNIT SIZE | 95°F AMBIENT |  |  |  |  | 105°F AMBIENT |  |  |  |  | 115°F AMBIENT |  |  |  |  | 118.4°F AMBIENT |  |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg)
ACSC080 | 78.1 | 82.9 | 10.1 | 187.4 | 15.2 | 71.7 | 92.9 | 8.4 | 172.1 | 12.9 | 64.8 | 104.1 | 6.9 | 155.5 | 10.6 | 62.3 | 108.1 | 6.4 | 149.5 | 9.9 | 57.4 | 119.5 | 5.5 | 137.8 | 8.5
ACSC090 | 87 | 101.3 | 9.4 | 208.9 | 18.9 | 79.3 | 113.4 | 7.8 | 190.4 | 15.9 | 71.1 | 126.8 | 6.3 | 170.5 | 12.7 | 68.1 | 131.7 | 5.8 | 163.4 | 11.9 | 62.3 | 141.4 | 5 | 149.6 | 9.9
ACSC100 | 100.3 | 106.3 | 10.1 | 240.8 | 24.9 | 94.5 | 123.8 | 8.3 | 226.7 | 22.2 | 87.6 | 143.1 | 6.8 | 210.3 | 19.2 | 85 | 149.9 | 6.3 | 204.1 | 18 | 79.8 | 162.9 | 5.5 | 191.5 | 15.9
ACSC110 | 107.3 | 113.2 | 10.2 | 257.5 | 13.4 | 98.3 | 126.7 | 8.5 | 236 | 11.3 | 88.6 | 141.9 | 6.9 | 212.6 | 9.2 | 85.1 | 147.4 | 6.4 | 204.3 | 8.5 | 78.3 | 158.4 | 5.6 | 182.9 | 7.4
ACSC120 | 117.6 | 130.3 | 9.9 | 282.2 | 15.9 | 110.3 | 151.7 | 8.1 | 264.8 | 14.1 | 101.8 | 174.8 | 6.5 | 244.4 | 12 | 98.6 | 182.9 | 6.1 | 236.6 | 11.3 | 92.1 | 198.3 | 5.2 | 221.1 | 9.9
ACSC130 | 122 | 146.2 | 9.6 | 304.8 | 18.5 | 116.4 | 169.7 | 7.8 | 279.4 | 16.9 | 108.5 | 195.1 | 6.3 | 260.4 | 13.6 | 105 | 204 | 5.8 | 252.2 | 12.9 | 97.6 | 220.7 | 4.9 | 235 | 11.3
ACSC140 | 135 | 134.3 | 10.8 | 324.1 | 24.3 | 127.4 | 156.6 | 8.9 | 305.8 | 21.7 | 118.9 | 181.4 | 7.2 | 284.2 | 18.7 | 115 | 189.4 | 7.7 | 276 | 17.8 | 108.1 | 207.4 | 5.8 | 259.4 | 15.7
ACSC160 | 158.3 | 184.5 | 9.5 | 379.8 | 32.8 | 147.8 | 214.2 | 7.7 | 354.7 | 28.9 | 135.7 | 246.1 | 6.2 | 325.6 | 24.5 | 131.1 | 257.2 | 5.8 | 314.6 | 22.9 | 122 | 278.4 | 5 | 292.7 | 19.9
ACSC180 | 175.6 | 191.3 | 10 | 421.5 | 13.6 | 165 | 222.8 | 8.2 | 395.9 | 12 | 152.4 | 257 | 6.6 | 365.7 | 10.4 | 147.6 | 269 | 6.1 | 354.3 | 9.7 | 138 | 292 | 5.3 | 331.3 | 8.5
ACSC190 | 187.8 | 213.1 | 9.7 | 450.8 | 15.5 | 175.7 | 247.5 | 7.9 | 421.7 | 13.6 | 161.5 | 284.6 | 6.4 | 387.6 | 11.3 | 156.2 | 297.6 | 5.9 | 374.8 | 10.9 | 145.5 | 322.5 | 5.1 | 349.2 | 9.5
ACSC200 | 192 | 209.6 | 10.3 | 460.8 | 14.1 | 181 | 239.6 | 8.4 | 436.6 | 12.5 | 168.2 | 276.4 | 6.8 | 403.6 | 10.9 | 163 | 289.3 | 6.3 | 391.2 | 10.2 | 152 | 313 | 5.5 | 366.1 | 9
ACSC210 | 203 | 216.9 | 10.3 | 487.3 | 15 | 190.4 | 252 | 8.4 | 456.9 | 13.6 | 176 | 290.6 | 6.7 | 422.6 | 11.8 | 170.1 | 304.3 | 6.3 | 408.2 | 11.1 | 158.8 | 330.8 | 5.2 | 381.2 | 9.7
ACSC220 | 214.7 | 242.5 | 9.9 | 515.3 | 15.2 | 200.8 | 281.5 | 8 | 481.9 | 13.4 | 184.6 | 323.6 | 6.5 | 443 | 11.3 | 178.5 | 338.4 | 6 | 428.5 | 10.6 | 166.3 | 366.7 | 5.2 | 399 | 9.2
ACSC240 | 231.8 | 251.1 | 10.2 | 556.4 | 17 | 217.5 | 291.8 | 8.3 | 522 | 15.7 | 200.7 | 336.4 | 6.7 | 481.8 | 13.4 | 194.5 | 352.1 | 6.2 | 466.8 | 12.6 | 181.8 | 382.4 | 5.4 | 436.3 | 11.2
ACSC250 | 243.4 | 275.8 | 9.9 | 584.2 | 19.4 | 227.7 | 320.3 | 8 | 546.5 | 17.1 | 209.3 | 368.3 | 6.4 | 502.3 | 14.6 | 202.5 | 390.6 | 5.9 | 486.1 | 13.6 | 188.6 | 417.5 | 5.2 | 452.7 | 11.8
ACSC260 | 252.5 | 294.1 | 9.6 | 606 | 20.8 | 235.6 | 340.9 | 7.8 | 565.4 | 18.5 | 215.9 | 391.4 | 6.4 | 518.1 | 15.5 | 208.5 | 409 | 5.8 | 500.3 | 14.4 | 193.8 | 442.3 | 5.2 | 465 | 12.5
ACSC270 | 261.7 | 277.7 | 10.4 | 628.1 | 15.3 | 245.2 | 323.5 | 8.5 | 588.9 | 13.5 | 227 | 372.6 | 6.9 | 544.8 | 11.6 | 220 | 390.3 | 6.3 | 528 | 10.9 | 205.8 | 424.2 | 5.5 | 493.8 | 9.6
ACSC280 | 271.8 | 294.5 | 10.2 | 652.3 | 16.4 | 254.7 | 342.1 | 8.5 | 611.3 | 14.6 | 227 | 363.5 | 6.7 | 545.3 | 11.6 | 221.2 | 412.6 | 6.2 | 545.3 | 12.2 | 212 | 448.1 | 5.4 | 508.9 | 10
ACSC300 | 290.7 | 310.4 | 10.3 | 697.8 | 12.2 | 265.8 | 346.8 | 8.5 | 639.3 | 10.5 | 239.1 | 387.4 | 6.9 | 573.7 | 8.5 | 229.4 | 402.1 | 6.4 | 550.5 | 7.9 | 210.7 | 431.2 | 5.5 | 505.6 | 6.7
ACSC310 | 299.6 | 330.1 | 10 | 719.1 | 13 | 273.5 | 368.5 | 8.3 | 656.3 | 10.9 | 245.5 | 411.6 | 6.7 | 589.1 | 9 | 235.4 | 427 | 6.2 | 564.9 | 8.2 | 215.8 | 457.8 | 5.3 | 518 | 7
ACSC320 | 308.7 | 349.8 | 9.8 | 740.8 | 13.8 | 281.2 | 390.5 | 8.1 | 675 | 11.5 | 251.9 | 435.7 | 6.5 | 604.6 | 9.3 | 241.4 | 452 | 6 | 580.4 | 8.6 | 220.9 | 484.5 | 5.2 | 530.2 | 7.3
ACSC330 | 319.5 | 362.7 | 9.8 | 766.8 | 14.6 | 298.8 | 420.9 | 8 | 717.1 | 12.9 | 274.5 | 483.8 | 6.4 | 658.8 | 11.1 | 265.5 | 505.8 | 6 | 637.2 | 10.4 | 247.3 | 548.1 | 5.1 | 593.4 | 9
ACSC350 | 352.5 | 379.4 | 9.7 | 846.1 | 14.3 | 321.3 | 442.4 | 8.1 | 771.1 | 12 | 276.1 | 471.3 | 6.6 | 689.5 | 9.7 | 275.3 | 511.5 | 6.1 | 660.9 | 9 | 251.9 | 547.7 | 5.2 | 604.6 | 8.4
ACSC365 | 369.1 | 406.6 | 10 | 885.8 | 16.2 | 346.2 | 472.6 | 8.2 | 830.9 | 13.2 | 309.2 | 569.4 | 6.4 | 766.1 | 19.8 | 309 | 569.8 | 6 | 742.1 | 18.7 | 288.8 | 617.5 | 5.3 | 693.2 | 16.2
ACSC380 | 380.2 | 441.2 | 9.8 | 936.5 | 28.6 | 364.9 | 511.8 | 8 | 875.6 | 25.2 | 335.3 | 588.2 | 6.4 | 805.7 | 21.2 | 320.1 | 615 | 5.9 | 777.9 | 20.3 | 301.9 | 666.5 | 5.2 | 724.5 | 17.6
ACSC400 | 390.2 | 441.2 | 9.8 | 936.5 | 28.6 | 364.9 | 511.8 | 8 | 875.6 | 25.2 | 335.3 | 588.2 | 6.4 | 805.7 | 21.2 | 324.1 | 615 | 5.9 | 777.9 | 20.3 | 301.9 | 666.5 | 5.2 | 724.5 | 17.6
ACSC420 | 406.9 | 457.5 | 9.9 | 977.5 | 27.5 | 380.1 | 530.6 | 8.2 | 912.7 | 24.3 | 348.8 | 609.9 | 6.5 | 832.2 | 20.6 | 333.2 | 637.7 | 6 | 808 | 19.2 | 313.7 | 691.3 | 5.2 | 752.8 | 16.9
ACSC450 | 463.6 | 502.2 | 10.7 | 1112.7 | 31.9 | 414.6 | 526.8 | 8.7 | 995.1 | 28.6 | 384.2 | 608.8 | 7.1 | 922.2 | 24.5 | 372.9 | 638.6 | 6.5 | 895 | 23.1 | 349.5 | 694.2 | 5.7 | 838.9 | 20.8
ACSC475 | 463.6 | 502.2 | 10.2 | 1112.7 | 35.8 | 435 | 583.5 | 8.4 | 1044 | 31.4 | 401.4 | 672.7 | 6.6 | 963.4 | 26.8 | 388.9 | 704.1 | 6.1 | 933.4 | 25.2 | 363.4 | 764.6 | 5.4 | 872 | 22.6
ACSC500 | 486.8 | 553 | 10 | 1168.3 | 38.8 | 455.4 | 640.5 | 8 | 1092.5 | 34.2 | 418.6 | 736.6 | 6.6 | 1004.8 | 29.3 | 404.9 | 770.4 | 6 | 971.9 | 27.3 | 377.3 | 835 | 5.2 | 905.5 | 24

## LCWT 44F
ACSC Performance Data (English System, 50Hz) — Leaving Chilled Water Temp 44°F
UNIT SIZE | 95°F AMBIENT |  |  |  |  | 105°F AMBIENT |  |  |  |  | 115°F AMBIENT |  |  |  |  | 118.4°F AMBIENT |  |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg)
ACSC080 | 81 | 84.1 | 10.4 | 194.4 | 16.4 | 74.4 | 94.1 | 8.6 | 178.6 | 13.9 | 67.3 | 105.4 | 7 | 161.5 | 11.6 | 64.8 | 109.5 | 6.5 | 155.5 | 10.6 | 59.7 | 117.7 | 5.6 | 143.4 | 9.2
ACSC090 | 90.2 | 102.8 | 9.6 | 216.5 | 20.3 | 82.3 | 115 | 7.9 | 197.4 | 15.9 | 73.7 | 128.5 | 6.4 | 177 | 13.6 | 70.7 | 133.5 | 5.9 | 169.8 | 12.7 | 64.8 | 143.2 | 5.1 | 155.4 | 10.6
ACSC100 | 103.7 | 107.2 | 10.4 | 248.9 | 26.6 | 97.8 | 125 | 8.5 | 234.6 | 23.6 | 90.8 | 144.7 | 6.9 | 217.9 | 20.6 | 88.2 | 151.6 | 6.4 | 211.6 | 19.4 | 82.8 | 164.9 | 5.6 | 198.7 | 17.1
ACSC110 | 111.3 | 114.6 | 10.5 | 267 | 14.3 | 102 | 128.4 | 8.7 | 244.8 | 12 | 92 | 143.7 | 7.1 | 220.8 | 9.9 | 88.4 | 149.3 | 6.6 | 212.2 | 9.2 | 81.4 | 160.3 | 5.7 | 195.4 | 7.9
ACSC120 | 121.6 | 131.8 | 9.9 | 291.8 | 17 | 114.3 | 153.5 | 8.3 | 274.4 | 15 | 105 | 177 | 6.7 | 253 | 12.7 | 102.2 | 185.3 | 6.2 | 245.3 | 12.2 | 95.1 | 201 | 5.4 | 229.2 | 10.6
ACSC130 | 130 | 148 | 9.6 | 312 | 21.5 | 122.7 | 171.9 | 7.9 | 294.4 | 19.5 | 110 | 196.5 | 6.6 | 270.6 | 13.6 | 109 | 206.9 | 6.1 | 261.6 | 13.6 | 101.5 | 223.6 | 5.2 | 243.6 | 12
ACSC140 | 139.7 | 135.7 | 11.1 | 335.4 | 25.9 | 131.9 | 158.8 | 9.1 | 316.5 | 23.1 | 122.6 | 183.3 | 7.4 | 294.3 | 20 | 119.2 | 192.3 | 6.9 | 286 | 18.9 | 112.1 | 209.6 | 6 | 269 | 16.9
ACSC160 | 163.6 | 186.7 | 9.7 | 392.7 | 34.9 | 152.9 | 217 | 7.9 | 366.7 | 30.7 | 140.4 | 249.5 | 6.4 | 336.9 | 26.1 | 135.8 | 260.9 | 5.9 | 325.9 | 24.5 | 126.4 | 282.5 | 5.1 | 303.4 | 21.3
ACSC180 | 181.6 | 193.4 | 10.1 | 435.9 | 14.6 | 170.7 | 225.4 | 8.4 | 409.7 | 12.9 | 157.8 | 260.2 | 6.8 | 378.7 | 11.1 | 152.9 | 272.4 | 6.3 | 367 | 10.4 | 143.2 | 295 | 5.5 | 343.6 | 9.2
ACSC190 | 194.1 | 215.7 | 9.9 | 465.9 | 16.6 | 181.7 | 250.6 | 8.1 | 436.2 | 14.6 | 167.2 | 288.3 | 6.6 | 401.3 | 12.2 | 161.8 | 301.6 | 6.1 | 388.2 | 11.6 | 150.9 | 327 | 5.3 | 362 | 10.2
ACSC200 | 200.1 | 206.3 | 10.6 | 480.1 | 15 | 188.2 | 242.4 | 8.6 | 451.7 | 13.4 | 174.1 | 279.8 | 7 | 418 | 11.6 | 169 | 293.1 | 6.5 | 405.5 | 10.9 | 158.4 | 316 | 5.6 | 379.7 | 9.5
ACSC210 | 209.9 | 219.1 | 10.3 | 503.7 | 16.4 | 196.9 | 254.9 | 8.4 | 472.6 | 14.6 | 181.8 | 294 | 6.8 | 436.2 | 12.5 | 176 | 307.7 | 6.3 | 422.6 | 11.9 | 164.3 | 334.5 | 5.5 | 394.5 | 10.3
ACSC220 | 221.9 | 245.7 | 10.1 | 532.5 | 16.2 | 207.6 | 285.2 | 8.2 | 498.3 | 13.6 | 191 | 328.1 | 6.6 | 458.4 | 12.2 | 184.8 | 343.3 | 6.1 | 443.5 | 11.6 | 172.3 | 372 | 5.3 | 413.5 | 9.9
ACSC240 | 239.7 | 254.1 | 10.4 | 575.4 | 18 | 225 | 295.4 | 8.5 | 540 | 15.9 | 207.8 | 340.7 | 6.9 | 498.7 | 14.3 | 201.3 | 356.7 | 6.4 | 483.2 | 13.6 | 188.4 | 387.5 | 5.6 | 452.1 | 11.9
ACSC250 | 251.7 | 279.4 | 10 | 604.1 | 20.6 | 235.5 | 324.4 | 8.2 | 565.1 | 18.2 | 216.6 | 373.4 | 6.6 | 519.8 | 15.5 | 209.6 | 390 | 6.1 | 503.1 | 14.6 | 195.9 | 423.9 | 5.3 | 470.3 | 12.7
ACSC260 | 261 | 298 | 9.8 | 626.4 | 22.1 | 243.5 | 345.6 | 7.9 | 584.5 | 19.4 | 223.3 | 396.9 | 6.4 | 536 | 16.4 | 215.9 | 415 | 5.9 | 518.1 | 15.4 | 200.8 | 452 | 5.1 | 481.9 | 13.1
ACSC270 | 270.6 | 280.9 | 10.6 | 649.5 | 15.7 | 253.5 | 327 | 8.7 | 610.2 | 14.3 | 234.5 | 376.6 | 7.1 | 564 | 12.2 | 227.9 | 395.5 | 6.5 | 546.9 | 11.7 | 213.4 | 429 | 5.7 | 512.7 | 10.3
ACSC280 | 280.8 | 298 | 10.4 | 674 | 17.3 | 263.4 | 346.4 | 8.6 | 632.2 | 15.2 | 235.9 | 390 | 6.7 | 566.3 | 12.2 | 235.3 | 418.7 | 6.3 | 564.8 | 13.2 | 219.9 | 454.3 | 5.5 | 527.8 | 10.9
ACSC300 | 301.3 | 315.1 | 10.5 | 723.1 | 12.9 | 275.5 | 351.8 | 8.7 | 661.3 | 11.1 | 248 | 392.8 | 7.1 | 595.2 | 9 | 238.1 | 407.6 | 6.6 | 571.4 | 8.4 | 219 | 436.9 | 5.7 | 525.5 | 7.2
ACSC310 | 310.3 | 335.5 | 10.2 | 744.6 | 13.9 | 283.5 | 374.1 | 8.5 | 680.3 | 11.7 | 254.5 | 417.3 | 6.9 | 610.8 | 9.7 | 244.2 | 433 | 6.4 | 586.2 | 8.8 | 224.5 | 463.9 | 5.5 | 538.7 | 7.5
ACSC320 | 319.5 | 355.2 | 10 | 766.7 | 14.6 | 291.4 | 396.4 | 8.3 | 699.4 | 12.3 | 261.1 | 442 | 6.7 | 626.6 | 9.9 | 250.4 | 458.4 | 6.2 | 600.9 | 9 | 229.4 | 490.9 | 5.4 | 550.6 | 7.8
ACSC330 | 330.1 | 367.3 | 10 | 792.4 | 15.6 | 309 | 426.5 | 8.2 | 741.5 | 13.6 | 284.1 | 490.5 | 6.6 | 681.8 | 11.8 | 274.9 | 513 | 6.1 | 659.7 | 11.1 | 256.2 | 556 | 5.3 | 614.9 | 9.7
ACSC350 | 365 | 402.7 | 9.7 | 876 | 16.4 | 333.9 | 452.8 | 8.3 | 801.4 | 13.9 | 286 | 464.4 | 6.7 | 686.3 | 9.9 | 286.7 | 532 | 6.2 | 688 | 11.1 | 251.9 | 535.2 | 5.4 | 627.2 | 9
ACSC365 | 377.4 | 409 | 10.3 | 905.9 | 17.4 | 354.6 | 455.9 | 8.6 | 851 | 14.6 | 312.6 | 507.6 | 6.6 | 798.5 | 21.2 | 312 | 526.9 | 6.4 | 775 | 20.4 | 280.7 | 562.8 | 5.5 | 650.7 | 8.5
ACSC380 | 393.5 | 416 | 10.4 | 945.3 | 29.1 | 369.8 | 484.3 | 8.6 | 888.2 | 26.1 | 332 | 558.1 | 6.9 | 797.7 | 21.8 | 331.5 | 584.7 | 6.4 | 795 | 21 | 310.1 | 634.8 | 5.6 | 744.4 | 18.3
ACSC400 | 416.6 | 452.8 | 10.3 | 999.9 | 32.5 | 389.6 | 525.4 | 8.4 | 935 | 30 | 358.6 | 604.5 | 6.7 | 860 | 24.3 | 347.1 | 632.4 | 6.2 | 833.3 | 22.7 | 320.6 | 685.6 | 5.4 | 770 | 20.3
ACSC420 | 433.8 | 469.9 | 10.3 | 1041 | 30.7 | 405.6 | 545.2 | 8.4 | 973.5 | 27 | 372.9 | 627.1 | 6.7 | 894.9 | 23.3 | 360.8 | 655.9 | 6.3 | 866 | 21.9 | 336.5 | 711.4 | 5.5 | 807.5 | 18.7
ACSC450 | 470.4 | 462.5 | 11.2 | 1129 | 34.5 | 443.5 | 538.9 | 9.1 | 1064.5 | 32.5 | 411.6 | 623.4 | 7.4 | 955 | 28.2 | 399.6 | 653.3 | 6.9 | 969.8 | 26.8 | 375.7 | 711.8 | 6 | 900.6 | 23.9
ACSC475 | 495.3 | 514.2 | 10.7 | 1188.7 | 40 | 458 | 591 | 8.7 | 1116.4 | 35.6 | 423.9 | 690.2 | 7 | 1031.6 | 30.5 | 416.6 | 722.7 | 6.5 | 1000 | 28.9 | 391 | 790 | 5.7 | 938.4 | 25.4
ACSC500 | 519.9 | 565.6 | 10 | 1247 | 41.7 | 486.6 | 657.5 | 8 | 1168.3 | 38.8 | 448 | 757 | 6.7 | 1130.6 | 34 | 419.3 | 781 | 6 | 1006.7 | 29.1 | 391 | 846.9 | 5.4 | 938.4 | 25.4

## LCWT 46F
ACSC Performance Data (English System, 50Hz) — Leaving Chilled Water Temp 46°F
UNIT SIZE | 95°F AMBIENT |  |  |  |  | 105°F AMBIENT |  |  |  |  | 115°F AMBIENT |  |  |  |  | 118.4°F AMBIENT |  |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg)
ACSC080 | 83.9 | 85.2 | 10.6 | 201.4 | 17.6 | 77.1 | 95.4 | 8.8 | 185.1 | 14.8 | 69.8 | 106.8 | 7.2 | 167.5 | 12.5 | 67.3 | 110.9 | 6.7 | 161.4 | 11.3 | 62.1 | 119.1 | 5.8 | 149 | 9.9
ACSC090 | 93.4 | 104.4 | 9.9 | 224.2 | 21.7 | 85.2 | 116.6 | 8.1 | 204.4 | 17.8 | 76.4 | 130.3 | 6.6 | 183.4 | 14.6 | 73.4 | 135.3 | 6.1 | 176.1 | 13.6 | 67.4 | 145 | 5.2 | 161.3 | 11.3
ACSC100 | 107.1 | 108.2 | 10.7 | 257.1 | 28.2 | 101.1 | 126.3 | 8.7 | 242.6 | 24.9 | 94 | 146.2 | 7.1 | 225.5 | 21.9 | 91.3 | 153.3 | 6.6 | 219.1 | 20.8 | 85.8 | 166.9 | 5.8 | 205.9 | 18.4
ACSC110 | 115.2 | 116.3 | 10.7 | 276.6 | 16.2 | 105.7 | 130.1 | 8.9 | 253.6 | 12.7 | 95.4 | 145.5 | 7.2 | 228.9 | 10.6 | 91.7 | 151.1 | 6.7 | 220.2 | 9.9 | 84.5 | 162.2 | 5.8 | 202.9 | 8.4
ACSC120 | 125.5 | 133.2 | 10.2 | 301.3 | 17.8 | 118 | 155.2 | 8.4 | 283.2 | 15.9 | 109 | 179.2 | 6.7 | 261.7 | 13 | 105.8 | 187.7 | 6.3 | 253.9 | 13.2 | 98.9 | 203.7 | 5.5 | 237.2 | 11.3
ACSC130 | 132 | 151.6 | 9.8 | 316.7 | 20.8 | 126.8 | 174.1 | 8.2 | 304.3 | 18.5 | 116 | 200.5 | 6.6 | 279.9 | 18.5 | 112.8 | 209.6 | 6.1 | 270.6 | 13.4 | 105 | 232.5 | 5.2 | 252 | 11.6
ACSC140 | 144.4 | 137 | 11.4 | 346.5 | 27.5 | 136 | 159.8 | 9.2 | 326.4 | 24.5 | 126.6 | 184.6 | 7.6 | 304.5 | 21.5 | 123.3 | 193.9 | 7 | 295.9 | 18.9 | 116.1 | 212.2 | 6.2 | 278.5 | 16.9
ACSC160 | 169 | 189 | 9.9 | 405.5 | 37 | 158 | 219.8 | 8.1 | 379.3 | 32.4 | 145.2 | 252.9 | 6.5 | 348.5 | 24.5 | 140.5 | 264.5 | 6 | 337.2 | 26 | 130.5 | 286.5 | 5.2 | 314.2 | 22.7
ACSC180 | 187.7 | 195.5 | 10.5 | 450.4 | 15.7 | 176.4 | 228 | 8.6 | 423.4 | 13.9 | 163.2 | 263.4 | 6.9 | 391.7 | 11.4 | 158.2 | 275.8 | 6.4 | 379.7 | 11.1 | 148.3 | 299.9 | 5.6 | 355.9 | 9.9
ACSC190 | 200.4 | 218.2 | 10.1 | 481 | 17.6 | 187.6 | 253.7 | 8.3 | 450 | 15.5 | 172.8 | 291.9 | 6.7 | 414.4 | 13.2 | 167.3 | 305.5 | 6.2 | 401 | 12.2 | 156.2 | 331.5 | 5.4 | 374.9 | 10.9
ACSC200 | 206.6 | 210.7 | 10.8 | 495.9 | 15.9 | 194.5 | 245.3 | 8.8 | 466.8 | 14.3 | 180.1 | 283.3 | 7.1 | 432 | 12.2 | 174.9 | 296.6 | 6.6 | 419.8 | 11.6 | 163.9 | 322 | 5.7 | 393.3 | 9.9
ACSC210 | 217 | 222 | 10.7 | 520.9 | 17.5 | 203.5 | 258.3 | 8.8 | 488.6 | 15.9 | 187.6 | 298 | 7.1 | 450.4 | 13.9 | 182.1 | 311.6 | 6.6 | 437 | 13.2 | 170 | 338 | 5.7 | 408 | 11.1
ACSC220 | 229 | 248.9 | 10.3 | 549.6 | 16.5 | 214.1 | 289 | 8.4 | 514 | 15.2 | 197.3 | 332.2 | 6.6 | 473.5 | 12.6 | 190.8 | 347.9 | 6.3 | 458 | 12 | 178 | 377.3 | 5.4 | 427 | 10.2
ACSC240 | 247.5 | 257.1 | 10.7 | 594.1 | 20 | 232.5 | 299 | 8.7 | 558 | 17.8 | 214.6 | 345.1 | 7 | 515.7 | 15.2 | 208.2 | 361.3 | 6.6 | 499.7 | 14.4 | 195 | 392.2 | 5.6 | 468 | 12
ACSC250 | 260 | 282 | 10.2 | 624.1 | 21.7 | 243.2 | 328.6 | 8.3 | 583.7 | 19.4 | 223.6 | 378.4 | 6.7 | 536.7 | 16.4 | 216.7 | 390.6 | 6.1 | 520.1 | 16.3 | 203.3 | 430.2 | 5.4 | 487.9 | 13.9
ACSC260 | 269.5 | 302 | 10 | 646.7 | 23.3 | 251.5 | 350.2 | 8.1 | 603.6 | 20.6 | 230.8 | 402.5 | 6.5 | 553.9 | 17.5 | 223.3 | 420.9 | 6.1 | 535.9 | 16.3 | 207.9 | 456.1 | 5.3 | 499 | 14.3
ACSC270 | 279.5 | 284.1 | 10.9 | 670.8 | 16.4 | 262.7 | 330.7 | 8.9 | 630.5 | 14.8 | 243 | 382 | 7.2 | 583.2 | 12.9 | 236.4 | 400.3 | 6.6 | 567.6 | 12.5 | 221.1 | 435.6 | 5.8 | 546.7 | 11
ACSC280 | 290.5 | 301.5 | 10.6 | 696.9 | 17.6 | 272.2 | 350.6 | 8.8 | 653 | 15 | 244 | 404.5 | 6.9 | 585 | 13.2 | 243.7 | 423.7 | 6.5 | 584.3 | 13.4 | 227.8 | 460.5 | 5.6 | 546.7 | 11.5
ACSC300 | 311.8 | 319.7 | 10.8 | 748.4 | 13.6 | 285.3 | 356.8 | 8.9 | 684.6 | 11.8 | 256.6 | 398.2 | 7.2 | 616.7 | 9.7 | 246.8 | 413 | 6.7 | 592.4 | 9 | 227 | 442.6 | 5.8 | 545.4 | 7.7
ACSC310 | 320.9 | 340.1 | 10.5 | 770.1 | 14.2 | 293.5 | 378.6 | 8.6 | 704.4 | 12.5 | 263.6 | 422.7 | 7 | 632.7 | 10.1 | 253.2 | 438 | 6.5 | 607.6 | 9.4 | 232.6 | 470 | 5.6 | 558.2 | 7.9
ACSC320 | 330.3 | 360.6 | 10.2 | 792.7 | 15.5 | 301.6 | 402.4 | 8.4 | 723.9 | 13.2 | 270.3 | 448.2 | 6.8 | 648.7 | 10.5 | 259.4 | 464.6 | 6.3 | 622.5 | 9.6 | 237.9 | 497.5 | 5.4 | 571.1 | 8.2
ACSC330 | 340.8 | 372 | 10.2 | 818 | 16.4 | 319.1 | 432.1 | 8.3 | 765.8 | 14.3 | 293.6 | 497.3 | 6.7 | 704.7 | 12.5 | 284.3 | 520.2 | 6.2 | 682.5 | 11.7 | 265.2 | 564 | 5.4 | 636.5 | 10.4
ACSC350 | 377.4 | 409 | 10.2 | 887.9 | 16.6 | 330.4 | 435 | 8.6 | 792.9 | 12.9 | 296.6 | 484.4 | 6.9 | 711.9 | 11 | 287.6 | 526.2 | 6.4 | 690.3 | 11.3 | 261.3 | 562.9 | 5.5 | 650.7 | 10.1
ACSC365 | 389.8 | 415.9 | 10.5 | 935.4 | 18.4 | 369.8 | 484.3 | 8.6 | 888.2 | 17.5 | 326.9 | 535.4 | 6.9 | 785.7 | 11.1 | 320.4 | 545.2 | 6.6 | 750 | 13.4 | 280.7 | 562.8 | 5.7 | 675.3 | 8.9
ACSC380 | 393.9 | 416.3 | 10.6 | 945.3 | 26.1 | 369.8 | 484.3 | 8.6 | 902.2 | 24.5 | 332 | 558.1 | 6.9 | 810.2 | 20.8 | 331.5 | 584.7 | 6.4 | 795 | 20.5 | 310.1 | 634.8 | 5.7 | 744.4 | 17.9
ACSC400 | 429.8 | 458.6 | 10.7 | 1031.6 | 34.2 | 389.6 | 525.4 | 8.4 | 955 | 30 | 358.6 | 604.5 | 6.7 | 860 | 24.3 | 347.1 | 632.4 | 6.2 | 833.3 | 22.7 | 320.6 | 685.6 | 5.4 | 770 | 20.3
ACSC420 | 433.8 | 469.9 | 10.3 | 1041 | 30.7 | 405.6 | 545.2 | 8.4 | 973.5 | 27 | 372.9 | 627.1 | 6.7 | 894.9 | 23.3 | 360.8 | 655.9 | 6.3 | 866 | 21.9 | 336.5 | 711.4 | 5.5 | 807.5 | 18.7
ACSC450 | 470.4 | 462.5 | 11.2 | 1129 | 38.8 | 443.5 | 538.9 | 9.1 | 1064.5 | 34.2 | 411.6 | 623.4 | 7.4 | 955 | 28.2 | 399.6 | 653.3 | 6.9 | 968.6 | 26.8 | 375.7 | 711.8 | 6 | 900.6 | 24.9
ACSC475 | 495.3 | 514.2 | 10.7 | 1188.7 | 40 | 459 | 598.1 | 8.7 | 1116.4 | 35.6 | 423.9 | 690.2 | 6.7 | 1031.6 | 30.5 | 416.6 | 722.7 | 6.1 | 1006 | 28.9 | 391 | 790 | 5.7 | 938.4 | 25.4
ACSC500 | 519.9 | 565.6 | 10.7 | 1247 | 45.7 | 486.6 | 657.5 | 8.7 | 1168.3 | 38.8 | 448 | 757 | 6.7 | 1206 | 41.1 | 462.7 | 767.2 | 6.4 | 1110.6 | 34.7 | 418.4 | 870.8 | 5.5 | 1004.1 | 25.4

## LCWT 48F
ACSC Performance Data (English System, 50Hz) — Leaving Chilled Water Temp 48°F
UNIT SIZE | 95°F AMBIENT |  |  |  |  | 105°F AMBIENT |  |  |  |  | 115°F AMBIENT |  |  |  |  | 118.4°F AMBIENT |  |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg)
ACSC080 | 86.8 | 86.3 | 10.9 | 208.4 | 18.7 | 79.8 | 96.6 | 9 | 191.6 | 15.7 | 72.5 | 108.1 | 7.4 | 173.9 | 13.4 | 69.7 | 110.9 | 6.9 | 167.4 | 12 | 64.4 | 120.6 | 6 | 154.6 | 10.6
ACSC090 | 96.6 | 105.9 | 10.1 | 231.9 | 23.1 | 88.1 | 118.2 | 8.3 | 211.4 | 18.7 | 79.2 | 132 | 6.7 | 189.9 | 15.6 | 76 | 137.1 | 6.2 | 182.4 | 14.6 | 70 | 146.8 | 5.4 | 168 | 12.2
ACSC100 | 110.5 | 109.1 | 10.9 | 265.3 | 29.8 | 104.4 | 127.6 | 9 | 250.6 | 26.3 | 97.1 | 147.8 | 7.3 | 233.3 | 22.9 | 94.4 | 155 | 6.8 | 226.6 | 22.2 | 88.8 | 168.8 | 5.9 | 213.5 | 19.4
ACSC110 | 119.2 | 117.9 | 11 | 286.1 | 16.2 | 109.4 | 131.8 | 9.1 | 262.5 | 13.4 | 98.8 | 147.4 | 7.3 | 237.1 | 11.3 | 95.1 | 153 | 6.9 | 228.2 | 10.6 | 87.7 | 164.2 | 6 | 210.4 | 8.8
ACSC120 | 129.5 | 134.6 | 10.6 | 310.9 | 18.7 | 121.8 | 157 | 8.7 | 292.5 | 16.9 | 112.7 | 181.4 | 7 | 270.5 | 13.9 | 109.4 | 190.1 | 6.5 | 262.5 | 13.4 | 102.2 | 206.3 | 5.6 | 245.4 | 12
ACSC130 | 137 | 151.6 | 9.9 | 328.8 | 21.9 | 130.6 | 176.4 | 8.3 | 313.4 | 19.6 | 120.5 | 203.2 | 6.7 | 289.2 | 13.4 | 117 | 212.5 | 6.2 | 280.8 | 14.7 | 108.7 | 230.5 | 5.3 | 260.8 | 13.4
ACSC140 | 149 | 138.3 | 11.6 | 357.7 | 29.8 | 140.8 | 161.4 | 9.6 | 338 | 26.3 | 131.1 | 187.3 | 7.7 | 314.7 | 22.9 | 127.5 | 196.5 | 7.1 | 305.8 | 18 | 120 | 214.6 | 6.2 | 288.1 | 19.4
ACSC160 | 174.3 | 191.3 | 10.1 | 418.4 | 39 | 163.2 | 222.6 | 8.3 | 391.6 | 34.4 | 150 | 256 | 6.7 | 359.9 | 29.3 | 145 | 268.2 | 6.1 | 348.5 | 27.7 | 135.4 | 290.6 | 5.3 | 324.9 | 24
ACSC180 | 193.7 | 197.6 | 10.6 | 464.9 | 16.4 | 182.2 | 230.5 | 8.8 | 437 | 14.8 | 168.6 | 266.6 | 7.1 | 404.7 | 12.5 | 163.5 | 279.3 | 6.6 | 392.5 | 11.8 | 153.6 | 303.6 | 5.7 | 368.6 | 11
ACSC190 | 206.7 | 220.8 | 10.4 | 496.1 | 18.9 | 193.8 | 256.9 | 8.5 | 465.1 | 16.4 | 178.5 | 295.9 | 6.9 | 428.4 | 13.9 | 172.9 | 309.8 | 6.3 | 415 | 13.2 | 161.5 | 336.1 | 5.6 | 386.9 | 11.6
ACSC200 | 213.2 | 213 | 11.1 | 511.7 | 16.9 | 200.8 | 248.1 | 9 | 482 | 15.2 | 186.1 | 286.7 | 7.3 | 446.6 | 12.9 | 180.9 | 300.6 | 6.8 | 434.2 | 12.2 | 169.6 | 326 | 5.9 | 406.4 | 9.9
ACSC210 | 218 | 215.5 | 11 | 533.2 | 19 | 210 | 261.4 | 8.8 | 504.1 | 16.7 | 194.1 | 301.6 | 7 | 465.5 | 13.9 | 188.1 | 316.1 | 6.7 | 451.4 | 13.3 | 175 | 335 | 5.9 | 425 | 12.5
ACSC220 | 236.2 | 251.9 | 10.5 | 566.8 | 18.2 | 221.2 | 292.7 | 8.6 | 531 | 16.2 | 203.8 | 337 | 6.9 | 489 | 13.4 | 197.3 | 352.7 | 6.4 | 473.4 | 12.7 | 184.4 | 382.3 | 5.5 | 442.5 | 11.2
ACSC240 | 255.4 | 260 | 10.9 | 613 | 21.1 | 240 | 302.6 | 8.9 | 575.9 | 18.9 | 222 | 349.6 | 7.3 | 532.7 | 16.2 | 215.6 | 365.8 | 6.7 | 517.4 | 15.4 | 201.6 | 397.8 | 5.8 | 483.8 | 13.5
ACSC250 | 268.3 | 286.5 | 10.5 | 644 | 22.6 | 250.9 | 332.8 | 8.5 | 602 | 20.6 | 231.1 | 383.4 | 6.9 | 554.7 | 17.3 | 223.8 | 390.6 | 6.3 | 537.1 | 16.4 | 210.6 | 449.6 | 5.5 | 505.5 | 14.6
ACSC260 | 277.9 | 305.9 | 10.2 | 667.1 | 24.6 | 259.5 | 354.9 | 8.3 | 622.7 | 21.7 | 238.2 | 408.1 | 6.7 | 571.8 | 18.2 | 230.7 | 426.9 | 6.2 | 553.6 | 17.2 | 215 | 462.7 | 5.5 | 515.9 | 15
ACSC270 | 288.4 | 287.3 | 11.1 | 692 | 17.5 | 271 | 334.6 | 9.1 | 650.7 | 15.6 | 251 | 386.7 | 7.3 | 602.5 | 13.5 | 244 | 403.6 | 6.8 | 584.8 | 13.3 | 228.8 | 440.1 | 5.9 | 565.6 | 12.2
ACSC280 | 299 | 304.4 | 11 | 717.2 | 18.4 | 280 | 351.4 | 8.9 | 672 | 16.4 | 251.4 | 386 | 7 | 603.3 | 15 | 251.6 | 429.2 | 6.7 | 603.5 | 15 | 235.7 | 464.8 | 5.7 | 565.6 | 11.8
ACSC300 | 322.4 | 324.4 | 11 | 773.7 | 14.3 | 295 | 361.9 | 9 | 708 | 12.5 | 265.9 | 403.5 | 7.4 | 638 | 10.1 | 256.5 | 418.5 | 6.9 | 615.3 | 9.2 | 235.5 | 448.3 | 6 | 565.3 | 7.8
ACSC310 | 331.5 | 345.1 | 10.7 | 795.6 | 14.9 | 303.5 | 385.1 | 8.8 | 728.4 | 13.2 | 272.5 | 428.9 | 7 | 654.1 | 10.6 | 262 | 444.9 | 6.6 | 628.7 | 9.9 | 240.9 | 476.2 | 5.7 | 578.3 | 8.4
ACSC320 | 341 | 366 | 10.4 | 818.8 | 16.3 | 311.8 | 408.3 | 8.6 | 748.2 | 14 | 279.5 | 454.4 | 6.9 | 670.8 | 11.2 | 268.4 | 471.2 | 6.4 | 644.1 | 10.2 | 246.4 | 504.1 | 5.7 | 591.5 | 8.7
ACSC330 | 351.4 | 376.6 | 10.4 | 843.4 | 17.3 | 329.3 | 437.7 | 8.5 | 790.2 | 15 | 303.2 | 504 | 6.8 | 727.6 | 13.2 | 293.6 | 527.4 | 6.4 | 704.7 | 12.5 | 274.2 | 571.9 | 5.5 | 658 | 11.1
ACSC350 | 389 | 415.3 | 10.5 | 897.7 | 17 | 343 | 447.5 | 8.7 | 819.7 | 13.9 | 309.5 | 491.6 | 7.1 | 742.6 | 11 | 294.6 | 509.7 | 6.6 | 707.1 | 11.3 | 270.7 | 545.4 | 5.6 | 649.6 | 8.5
ACSC365 | 389.8 | 415.9 | 10.7 | 945.7 | 18.4 | 369.8 | 484.3 | 8.6 | 888.2 | 17.5 | 326.9 | 535.4 | 6.9 | 785.7 | 21.2 | 320.4 | 545.2 | 6.6 | 750 | 20.4 | 280.7 | 562.8 | 5.7 | 675.3 | 8.5
ACSC380 | 406.3 | 421.1 | 10.6 | 975.7 | 28.1 | 369.8 | 490.2 | 8.7 | 924 | 26 | 351.4 | 565.6 | 7.1 | 834.3 | 21.9 | 342.3 | 592.4 | 6.6 | 821.4 | 21.9 | 320.8 | 643.5 | 5.7 | 769.9 | 18.9
ACSC400 | 429.8 | 458.6 | 10.7 | 1031.6 | 34.2 | 401.9 | 532.9 | 8.4 | 964.6 | 30 | 370.2 | 612.7 | 6.7 | 888.5 | 25.5 | 358.6 | 641 | 6.2 | 860.7 | 24.3 | 334.8 | 695.5 | 5.4 | 805.5 | 21.7
ACSC420 | 447.2 | 476.1 | 10.5 | 1073 | 32.3 | 418.4 | 552.5 | 8.6 | 1004.2 | 28.4 | 384.9 | 635.7 | 6.9 | 923.7 | 24.7 | 372.6 | 665 | 6.4 | 894.1 | 23.3 | 347.9 | 721.5 | 5.6 | 834.9 | 19.6
ACSC450 | 485.4 | 467.4 | 11.4 | 1164.9 | 38.8 | 458 | 544.8 | 9.6 | 1099.2 | 34.2 | 425.3 | 630.8 | 7.4 | 1020 | 30 | 412.9 | 661.2 | 7 | 990.9 | 28.6 | 388.1 | 720.6 | 6.1 | 931.5 | 24.9
ACSC475 | 511.1 | 520.2 | 10.9 | 1226.7 | 42.3 | 485.3 | 514.2 | 8.9 | 1152.6 | 52.7 | 444 | 699 | 7 | 1065.7 | 32.3 | 416.6 | 722.7 | 6.5 | 1006.6 | 28.9 | 403.5 | 795.7 | 5.7 | 968.4 | 25.4
ACSC500 | 536.4 | 572.8 | 10.6 | 1287.4 | 45.7 | 502.9 | 666 | 8.7 | 1206.1 | 41.1 | 462.7 | 767.2 | 7.2 | 1110.6 | 34.7 | 447.5 | 792.5 | 6.4 | 1074.9 | 32.5 | 418.4 | 870.8 | 5.5 | 1004.1 | 28.6

## LCWT 50F
ACSC Performance Data (English System, 50Hz) — Leaving Chilled Water Temp 50°F
UNIT SIZE | 95°F AMBIENT |  |  |  |  | 105°F AMBIENT |  |  |  |  | 115°F AMBIENT |  |  |  |  | 118.4°F AMBIENT |  |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | EER | WFR (GPM) | WPD (ft.wg)
ACSC080 | 89.8 | 87.5 | 11.2 | 215.4 | 19.9 | 82.5 | 97.9 | 9.3 | 198.1 | 16.6 | 74.8 | 109.4 | 7.6 | 179.6 | 14.3 | 72.2 | 109.4 | 7.1 | 173.4 | 12.7 | 66.7 | 122.6 | 6.1 | 160.2 | 11.3
ACSC090 | 99.8 | 107.4 | 10.3 | 239.5 | 24.5 | 91 | 119.8 | 8.5 | 218.4 | 19.6 | 81.8 | 133.7 | 6.9 | 196.2 | 16.4 | 78.6 | 138.9 | 6.4 | 188.7 | 15.5 | 72.1 | 148.7 | 5.5 | 173 | 12.7
ACSC100 | 113.9 | 110.1 | 11.2 | 273.4 | 31.4 | 107.7 | 128.7 | 9.2 | 258.5 | 27.7 | 100.3 | 149.4 | 7.5 | 240.8 | 24.7 | 97.6 | 156.7 | 6.9 | 234.2 | 23.6 | 91.8 | 170.8 | 6 | 220.3 | 20.6
ACSC110 | 123.2 | 119.4 | 11.2 | 295.6 | 17.1 | 113 | 133.5 | 9.3 | 271.1 | 14.1 | 102.2 | 149.2 | 7.6 | 245.3 | 12 | 98.4 | 154.9 | 7.1 | 236.1 | 11.3 | 90.8 | 166.1 | 6.1 | 217.9 | 9.2
ACSC120 | 133.5 | 136 | 10.8 | 320.4 | 19.6 | 125.8 | 158.8 | 8.9 | 301.5 | 17.8 | 116.3 | 183.6 | 7.1 | 279 | 15.7 | 113 | 192.5 | 6.6 | 271.1 | 15 | 105.6 | 209 | 5.7 | 253.4 | 13.4
ACSC130 | 142.5 | 153 | 10 | 345.7 | 23.1 | 126.8 | 174.8 | 8.3 | 304.3 | 20.8 | 124 | 205.9 | 6.6 | 297.5 | 19.6 | 120.3 | 203.2 | 6.6 | 288.7 | 18.5 | 108.7 | 233.3 | 5.5 | 260.8 | 14.1
ACSC140 | 153.7 | 139.6 | 11.6 | 369 | 30.7 | 140.8 | 161.4 | 9.6 | 338 | 29.4 | 131.1 | 187.3 | 7.6 | 314.7 | 24.5 | 125.2 | 219.4 | 7.1 | 300.5 | 19.4 | 116.1 | 212.2 | 6.2 | 289.8 | 21
ACSC160 | 174.3 | 191.3 | 9.9 | 418.5 | 41.1 | 163.5 | 222.6 | 8.4 | 392.4 | 36.3 | 154.7 | 259 | 6.8 | 371.4 | 31 | 150 | 272 | 6.1 | 360.4 | 29.5 | 139 | 294.7 | 5.4 | 334 | 24
ACSC180 | 199.7 | 199.7 | 11 | 479 | 16.4 | 187.9 | 233.1 | 9 | 450.9 | 15.7 | 174 | 269.8 | 7.3 | 417.7 | 13.2 | 168.7 | 282.7 | 6.8 | 405 | 12.5 | 158.5 | 307.7 | 5.8 | 380.4 | 11.3
ACSC190 | 213 | 223.3 | 10.6 | 511.2 | 18.9 | 199.8 | 259.8 | 8.6 | 479.5 | 16.4 | 184.1 | 299.7 | 7 | 441.9 | 15.2 | 178.5 | 313.8 | 6.5 | 428.4 | 13.6 | 166.9 | 340.6 | 5.6 | 400.5 | 12.2
ACSC200 | 218.8 | 215.3 | 11.3 | 524.6 | 16.9 | 207.1 | 250 | 9 | 497.1 | 15.2 | 192.1 | 290.2 | 7.5 | 460.9 | 13.6 | 185.9 | 304.4 | 7 | 448.5 | 12.9 | 175.2 | 331.1 | 6 | 420.5 | 10.9
ACSC210 | 243.3 | 255 | 11 | 584 | 18.8 | 228 | 296.5 | 9.1 | 547.4 | 19 | 210.3 | 341.2 | 7.3 | 504.7 | 15.3 | 203.5 | 357.6 | 6.7 | 488.4 | 15.9 | 190.4 | 388 | 5.8 | 456.9 | 12.5
ACSC220 | 243.3 | 255 | 11.1 | 584 | 22.3 | 228 | 296.5 | 9.1 | 547.4 | 19.9 | 210.3 | 341.2 | 7.3 | 504.7 | 17.1 | 203.5 | 357.6 | 6.7 | 488.8 | 16.3 | 190.4 | 388 | 5.8 | 456.9 | 14
ACSC240 | 263.3 | 265 | 11.1 | 631.8 | 22.3 | 247.4 | 306.6 | 9.1 | 593.5 | 19.9 | 229 | 353.8 | 7.3 | 549.7 | 17.1 | 221.9 | 370.4 | 6.8 | 532.5 | 16.3 | 208.2 | 402.9 | 5.9 | 499.6 | 14
ACSC250 | 276.7 | 290 | 10.7 | 664 | 24 | 258.7 | 337 | 8.7 | 620.8 | 21.7 | 238.4 | 388.5 | 6.9 | 572.2 | 18.2 | 230.9 | 390.6 | 6.3 | 554.1 | 17.3 | 217.9 | 443 | 5.5 | 523.1 | 15.5
ACSC260 | 286.4 | 309.9 | 10.4 | 687.4 | 25.9 | 267.4 | 359.6 | 8.4 | 641.8 | 22.9 | 245.7 | 413.7 | 6.8 | 589.7 | 19.2 | 238.1 | 432.9 | 6.3 | 571.4 | 18.1 | 222 | 469.3 | 5.4 | 532.9 | 16.2
ACSC270 | 297.3 | 290.7 | 11.6 | 713.6 | 18.9 | 280 | 341 | 9.4 | 671 | 16.7 | 259 | 391.6 | 7.6 | 621.7 | 14.8 | 251.5 | 410.4 | 7 | 603.7 | 14.4 | 235.9 | 447 | 6 | 566.2 | 13.2
ACSC280 | 308 | 304.2 | 11.2 | 739.1 | 20 | 289 | 366.9 | 9 | 693.4 | 17.8 | 267.7 | 414.6 | 7.2 | 642.5 | 15.5 | 259.7 | 434.7 | 6.7 | 623.4 | 15 | 243.6 | 475.5 | 5.8 | 565.6 | 12.5
ACSC300 | 332.9 | 329 | 11.2 | 799 | 15 | 304.7 | 366.6 | 9.3 | 731.4 | 13.2 | 274.9 | 408.8 | 7.6 | 659.7 | 10.9 | 264.3 | 424 | 7 | 634.2 | 9.7 | 243 | 454 | 6.1 | 585.1 | 8.5
ACSC310 | 342.1 | 350.1 | 10.9 | 821.1 | 15 | 313.5 | 386 | 9 | 752.6 | 14 | 281.6 | 434.6 | 7.3 | 675.8 | 11.1 | 270.8 | 450.8 | 6.8 | 650 | 10.4 | 249.3 | 482.3 | 5.9 | 598.3 | 8.9
ACSC320 | 351.9 | 371.4 | 10.6 | 844.5 | 17.2 | 321.9 | 414.2 | 8.8 | 772.7 | 14.9 | 288.7 | 460.7 | 7.1 | 692.9 | 11.5 | 277.4 | 477.6 | 6.6 | 665.8 | 11.1 | 254.9 | 510.7 | 5.7 | 611.9 | 9.2
ACSC330 | 362 | 381.2 | 10.6 | 868.9 | 17.7 | 339 | 443.6 | 8.7 | 814.6 | 15.7 | 312.7 | 510.7 | 6.9 | 750.5 | 13.9 | 303 | 534.5 | 6.5 | 727.3 | 13.2 | 283.1 | 579.9 | 5.6 | 679.5 | 11.8
ACSC350 | 402 | 421.6 | 10.7 | 965.3 | 18 | 357 | 447.7 | 8.8 | 856.5 | 14.8 | 316.5 | 541.1 | 7.1 | 759.5 | 11.7 | 305.1 | 541 | 6.7 | 732 | 12.8 | 280.7 | 552.5 | 5.8 | 672.6 | 9.9
ACSC365 | 402 | 421.6 | 11 | 965.3 | 18.8 | 393.5 | 496.1 | 8.7 | 944.3 | 18.5 | 316.5 | 541.1 | 6.9 | 759.5 | 15 | 305.1 | 541 | 6.7 | 732 | 12 | 280.7 | 552.5 | 5.8 | 672.6 | 12
ACSC380 | 418.7 | 427.2 | 10.9 | 1004.9 | 29.9 | 393.5 | 496.1 | 8.8 | 944.3 | 25.2 | 353.3 | 571 | 7.1 | 847.9 | 23.1 | 343.2 | 599 | 6.6 | 829.4 | 23.1 | 331.5 | 652.2 | 5.7 | 795.5 | 19.9
ACSC400 | 443 | 464.4 | 10.7 | 1063.2 | 36.4 | 414.3 | 539.7 | 8.7 | 994.3 | 31.6 | 381.8 | 620.8 | 7 | 916.4 | 27 | 370.1 | 649.7 | 6.5 | 888.3 | 24.9 | 345.8 | 704.8 | 5.6 | 829.8 | 23.1
ACSC420 | 460.7 | 484.4 | 10.7 | 1105.6 | 34 | 431.2 | 559.7 | 8.8 | 1034.8 | 29.8 | 396.9 | 644.3 | 7 | 952.5 | 26.1 | 384.4 | 674.1 | 6.5 | 922.5 | 24.7 | 359.3 | 731.6 | 5.6 | 862.2 | 20.6
ACSC450 | 500.3 | 472.2 | 11.7 | 1200.8 | 41.1 | 472 | 550 | 9.6 | 1133 | 36 | 439 | 638.1 | 7.6 | 1053.6 | 31.9 | 426.2 | 669 | 7.2 | 1024 | 30.5 | 401 | 729.4 | 6.2 | 962.4 | 26.5
ACSC475 | 527 | 526.2 | 11.1 | 1264.7 | 44.6 | 495.5 | 612.6 | 9.1 | 1188.8 | 38.7 | 458.2 | 707.2 | 7.3 | 1099.8 | 34.2 | 445 | 741.2 | 6.8 | 1066.2 | 32.5 | 416.6 | 806.9 | 6 | 999.9 | 28.9
ACSC500 | 553 | 579.8 | 10.7 | 1327.1 | 48 | 519.9 | 674.8 | 8.7 | 1245.8 | 43.5 | 477.5 | 775.7 | 7.1 | 1145.9 | 36.5 | 462.2 | 803 | 6.4 | 1109.3 | 34.7 | 418.4 | 882.7 | 5.6 | 1004.1 | 25.4