## LCWT 40F
DHAC Performance Data (English System) — Leaving Chilled Water Temp 40°F
UNIT SIZE | 95°F AMBIENT |  |  |  | 105°F AMBIENT |  |  |  | 115°F AMBIENT |  |  |  | 118.4°F AMBIENT |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg)
DHAC-020 | 18.8 | 19.2 | 45.2 | 8.1 | 17.5 | 21.4 | 42 | 7.4 | 16.3 | 23.8 | 39.2 | 6.2 | 15.8 | 24.8 | 37.9 | 6.7 | 14.8 | 26.6 | 35.6 | 7.4
DHAC-025 | 23.1 | 22.4 | 55.3 | 9 | 21.6 | 24.8 | 51.8 | 8.1 | 19.9 | 27.6 | 47.8 | 6.7 | 19.4 | 28.6 | 46.5 | 6.5 | 18.2 | 30.8 | 43.6 | 5.5
DHAC-030 | 27.9 | 31 | 67 | 13.9 | 26.1 | 34.2 | 62.6 | 11.8 | 24.1 | 38.2 | 57.8 | 10.2 | 23.5 | 39.7 | 56 | 9.5 | 22 | 42.5 | 52.6 | 7.8
DHAC-035 | 31.9 | 28 | 76.5 | 4.9 | 30.1 | 31 | 72.2 | 4.4 | 28 | 35 | 67.2 | 3.7 | 27.4 | 36.5 | 65.3 | 3.7 | 25.7 | 39.2 | 61.7 | 3.2
DHAC-040 | 37.2 | 35.2 | 89.3 | 6.9 | 35 | 39.4 | 84.1 | 6.2 | 32.4 | 44.2 | 77.6 | 5.3 | 31.6 | 46 | 75.4 | 5.1 | 29.7 | 49.6 | 71.3 | 4.9
DHAC-050 | 46.9 | 47.8 | 112.5 | 10.6 | 43.6 | 53.2 | 104.5 | 9 | 40.3 | 59.4 | 96.6 | 7.6 | 39.2 | 61.6 | 94 | 6.9 | 36.6 | 66.4 | 88.3 | 6.7
DHAC-060 | 60.1 | 55.1 | 144.4 | 5.7 | 56.7 | 61.4 | 136.2 | 5.5 | 52.4 | 68.8 | 125.6 | 4.5 | 51 | 71.4 | 122.5 | 4.3 | 47.5 | 76.9 | 114.9 | 9.2
DHAC-070 | 65.2 | 65.1 | 156.5 | 9.9 | 61.2 | 72.8 | 146.9 | 8.9 | 56.6 | 81.4 | 135.6 | 7.6 | 55.1 | 84.7 | 131.3 | 8 | 51.3 | 91.1 | 123.7 | 6.8
DHAC-075 | 69.8 | 72.3 | 167.4 | 13.4 | 65.2 | 80 | 156.8 | 12 | 60.4 | 89.1 | 144.9 | 10.2 | 59 | 92.7 | 141.2 | 9.5 | 55.2 | 99.9 | 132.6 | 8.3
DHAC-080 | 72.5 | 69.6 | 174 | 4 | 69.1 | 81.3 | 165.9 | 5.8 | 64.2 | 90.6 | 154.1 | 5.1 | 62.4 | 93.6 | 148.8 | 5.3 | 58 | 100.8 | 140.6 | 4.9
DHAC-095 | 89.1 | 96.3 | 213.8 | 7.6 | 83.1 | 106.2 | 199.5 | 6.6 | 76.7 | 117 | 184 | 5.8 | 75 | 121 | 178.2 | 5.1 | 70.2 | 128.7 | 168.6 | 4.9
DHAC-100 | 93.3 | 95.6 | 224 | 7.4 | 86.7 | 107.2 | 208.1 | 6.6 | 80 | 118.8 | 192.1 | 5.3 | 78 | 124 | 186.8 | 5.1 | 73.7 | 133.2 | 176.9 | 4.9

## LCWT 42F
DHAC Performance Data (English System) — Leaving Chilled Water Temp 42°F
UNIT SIZE | 95°F AMBIENT |  |  |  | 105°F AMBIENT |  |  |  | 115°F AMBIENT |  |  |  | 118.4°F AMBIENT |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg)
DHAC-020 | 19.5 | 19.4 | 46.8 | 8.8 | 18.2 | 21.6 | 43.6 | 7.9 | 17 | 24 | 40.4 | 6.7 | 16.3 | 25 | 39.2 | 6.7 | 15.3 | 26.8 | 36.8 | 6.7
DHAC-025 | 23.9 | 22.6 | 57.3 | 9.7 | 22.3 | 25 | 53.7 | 9.5 | 20.5 | 28.2 | 49.4 | 7.2 | 20.1 | 29 | 48.2 | 6.9 | 18.9 | 31 | 45.3 | 6
DHAC-030 | 28.6 | 31.5 | 69.1 | 14.6 | 26.9 | 34.7 | 64.6 | 12.9 | 24.8 | 38.6 | 59.5 | 10.4 | 24.2 | 40 | 58.2 | 11.8 | 22.9 | 42.8 | 55 | 8.5
DHAC-035 | 33.1 | 28.2 | 79.5 | 5.4 | 31.2 | 31.4 | 74.8 | 4.6 | 29.1 | 35.2 | 69.8 | 4.2 | 28.4 | 36.6 | 68 | 3.9 | 26.7 | 39.3 | 64.3 | 3.5
DHAC-040 | 38.5 | 35.4 | 92.5 | 7.6 | 36.2 | 39.6 | 86.9 | 6.6 | 33.5 | 44.4 | 80.4 | 5.6 | 32.6 | 46.2 | 78.3 | 5.5 | 30.9 | 50 | 74.1 | 5.1
DHAC-050 | 48.3 | 48.4 | 116 | 11.3 | 45 | 53.7 | 107.9 | 9.5 | 41.7 | 60 | 100 | 8.1 | 40.5 | 62.2 | 97.2 | 7.6 | 38 | 67 | 91.2 | 7
DHAC-060 | 61.9 | 55.4 | 148.6 | 6 | 58.5 | 61.9 | 140.4 | 5.7 | 54.1 | 70.4 | 129.9 | 4.9 | 52.7 | 73 | 126.5 | 4.7 | 49.9 | 77.4 | 119.8 | 9.9
DHAC-070 | 67.5 | 65.7 | 162 | 10.7 | 63 | 73 | 151.3 | 9.5 | 58.4 | 81.9 | 140.6 | 8.1 | 57.3 | 84.9 | 136.4 | 8.9 | 53.6 | 91.4 | 128.2 | 7.7
DHAC-075 | 72.4 | 73 | 173.7 | 14.5 | 67.6 | 80.7 | 162.3 | 13 | 62.6 | 89.8 | 150.2 | 11 | 61.5 | 93 | 147.5 | 10.2 | 57.4 | 100.5 | 137.7 | 9
DHAC-080 | 75.1 | 70.1 | 180.2 | 4.4 | 71.6 | 81.9 | 171.9 | 6.1 | 66.7 | 91.6 | 160 | 5.4 | 64.9 | 94.5 | 154.8 | 5.1 | 60.7 | 102 | 145.5 | 4.4
DHAC-095 | 92.5 | 96.8 | 220.6 | 8.1 | 86.4 | 107.4 | 207.4 | 7.1 | 79.8 | 118.3 | 191.5 | 6.2 | 78 | 122.1 | 184.3 | 5.5 | 72.9 | 129.4 | 175 | 5.1
DHAC-100 | 96.3 | 96.8 | 231.1 | 7.9 | 89.8 | 108 | 215.4 | 6.9 | 83.1 | 120 | 199.4 | 5.8 | 80.7 | 124.8 | 193.6 | 5.5 | 76.2 | 134 | 182.8 | 5.1

## LCWT 44F
DHAC Performance Data (English System) — Leaving Chilled Water Temp 44°F
UNIT SIZE | 95°F AMBIENT |  |  |  | 105°F AMBIENT |  |  |  | 115°F AMBIENT |  |  |  | 118.4°F AMBIENT |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg)
DHAC-020 | 20.2 | 19.6 | 48.4 | 9.5 | 18.8 | 21.8 | 45.2 | 8.3 | 17.3 | 24.2 | 41.6 | 6.7 | 16.9 | 25.2 | 40.4 | 6.7 | 15.8 | 27 | 38 | 6
DHAC-025 | 24.7 | 22.9 | 59.3 | 10.4 | 23 | 25.2 | 55.2 | 9.5 | 21.3 | 28 | 51.1 | 7.6 | 20.8 | 29 | 49.9 | 7.4 | 19.6 | 31.2 | 47 | 6.5
DHAC-030 | 29.7 | 31.4 | 71.2 | 15.2 | 27.8 | 35 | 66.7 | 13.6 | 25.6 | 39 | 61.4 | 11.8 | 25.1 | 40.4 | 60.2 | 11.1 | 23.6 | 43.2 | 56.4 | 9.5
DHAC-035 | 34.4 | 28.4 | 82.5 | 5.8 | 32.2 | 31.6 | 77.3 | 5.1 | 30.1 | 35.4 | 72.3 | 4.4 | 29.2 | 36.8 | 70 | 4.1 | 27.8 | 39.6 | 66.8 | 3.7
DHAC-040 | 39.9 | 35.6 | 95.7 | 8.5 | 37.5 | 40 | 90 | 7.3 | 34.7 | 44.8 | 83.3 | 6.2 | 33.8 | 46.4 | 81 | 6 | 32 | 50.4 | 76.6 | 5.3
DHAC-050 | 49.7 | 49 | 119.5 | 12 | 46.6 | 54.4 | 111.8 | 10.4 | 43.1 | 60.5 | 103.3 | 9 | 41.8 | 62.8 | 100.4 | 8.5 | 39.3 | 68 | 94.9 | 7.6
DHAC-060 | 63.6 | 55.7 | 152.5 | 6.5 | 60 | 62.2 | 143.8 | 6 | 55.5 | 69.6 | 133.1 | 4.9 | 54.1 | 72.5 | 129.7 | 4.7 | 50.8 | 78 | 120 | 10.6
DHAC-070 | 67 | 64.6 | 160.7 | 11.5 | 62.7 | 71 | 146.3 | 10.1 | 58 | 82.4 | 145.4 | 8.8 | 56.6 | 85.2 | 141.4 | 9.3 | 53.2 | 92 | 141.6 | 9.7
DHAC-075 | 75.7 | 73.5 | 167.5 | 13.6 | 70.9 | 81.2 | 168.4 | 15 | 65.5 | 90.6 | 156.8 | 12.7 | 64.2 | 94.2 | 150.1 | 10.9 | 60 | 101.4 | 141.6 | 9.7
DHAC-080 | 79.6 | 74.4 | 190.4 | 7.6 | 74.2 | 82.5 | 178 | 6.7 | 68.9 | 92.4 | 164.1 | 5.6 | 67.4 | 95.7 | 159.7 | 5.3 | 63 | 102.4 | 150.5 | 4.9
DHAC-095 | 94.8 | 98.7 | 227.4 | 8.5 | 88.4 | 108.6 | 212.1 | 7.4 | 81.6 | 119.4 | 195.9 | 6.5 | 79.6 | 123.4 | 189 | 5.7 | 74.7 | 131.1 | 179.4 | 5.5
DHAC-100 | 99.3 | 98 | 238.3 | 8.3 | 92.8 | 108.8 | 222.4 | 7.4 | 86.1 | 121.2 | 206.8 | 6 | 83.5 | 125.6 | 200.4 | 6 | 78.6 | 134.8 | 188.7 | 5.3

## LCWT 46F
DHAC Performance Data (English System) — Leaving Chilled Water Temp 46°F
UNIT SIZE | 95°F AMBIENT |  |  |  | 105°F AMBIENT |  |  |  | 115°F AMBIENT |  |  |  | 118.4°F AMBIENT |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg)
DHAC-020 | 20.8 | 19.8 | 50 | 10.2 | 19.5 | 22 | 46.8 | 8.8 | 18 | 24.4 | 42.8 | 7.6 | 17.4 | 25.4 | 41.7 | 7 | 16.3 | 27.2 | 39.2 | 5.3
DHAC-025 | 25.5 | 23 | 61.3 | 11.1 | 23.8 | 25.4 | 57 | 9.5 | 22 | 28.2 | 52.8 | 8.1 | 21.5 | 29.2 | 51.5 | 7.9 | 20.2 | 31.4 | 48.7 | 6.9
DHAC-030 | 30.8 | 31.6 | 73.4 | 15.9 | 28.6 | 35.4 | 68.7 | 14.6 | 26.6 | 39.4 | 63.7 | 11.8 | 25.9 | 40.8 | 62.2 | 11.8 | 24.3 | 43.6 | 58.2 | 10.2
DHAC-035 | 35.6 | 28.6 | 85.6 | 6.5 | 33.6 | 31.8 | 80.5 | 5.7 | 31.2 | 35.6 | 75 | 4.9 | 30.5 | 37 | 73 | 4.6 | 28.9 | 39.8 | 69.5 | 3.9
DHAC-040 | 41.2 | 35.8 | 99 | 9 | 38.6 | 40 | 92.6 | 7.6 | 35.6 | 44.8 | 85.4 | 6.6 | 34.8 | 46.6 | 83.6 | 6.4 | 33 | 50.6 | 79.5 | 5.5
DHAC-050 | 51.3 | 49.6 | 123.2 | 12.7 | 47.8 | 55 | 114.6 | 11.1 | 44.2 | 61.2 | 106.1 | 9.5 | 43.2 | 63 | 103.6 | 8.9 | 40.6 | 68.6 | 97.6 | 8.1
DHAC-060 | 65.1 | 65.4 | 148.6 | 18 | 61.6 | 72 | 148.6 | 11.7 | 55.4 | 69.8 | 133 | 8.5 | 55.1 | 81.6 | 123.6 | 8 | 51.5 | 87.4 | 123 | 6.6
DHAC-070 | 71.5 | 74.1 | 185.5 | 16.2 | 71.9 | 82.7 | 172.6 | 14.5 | 66.7 | 91.8 | 160 | 12.5 | 65.2 | 95.5 | 156.9 | 11.6 | 60.9 | 107.1 | 146.1 | 10.4
DHAC-075 | 81.9 | 75 | 196.6 | 8.1 | 78.5 | 83.4 | 184 | 8.1 | 72.8 | 92.8 | 171 | 7 | 71 | 96.5 | 165.5 | 6.6 | 66.3 | 103.9 | 156 | 6
DHAC-080 | 81.9 | 75 | 196.6 | 8.1 | 76.5 | 83.1 | 184 | 7 | 71 | 93 | 170.4 | 6 | 69.2 | 96.3 | 165.2 | 6 | 64.6 | 103.8 | 154.6 | 5.1
DHAC-095 | 97.7 | 99.4 | 234.2 | 9 | 91 | 109.6 | 218 | 7.6 | 84 | 120.6 | 201 | 6.6 | 82 | 124.5 | 195 | 6 | 76.5 | 132 | 184 | 5.5
DHAC-100 | 102.3 | 99.2 | 245.4 | 8.8 | 95.9 | 109.6 | 230.1 | 7.6 | 89.2 | 122.4 | 214.1 | 6 | 86.3 | 126.8 | 206.7 | 6 | 81.1 | 135.6 | 194.6 | 5.5

## LCWT 48F
DHAC Performance Data (English System) — Leaving Chilled Water Temp 48°F
UNIT SIZE | 95°F AMBIENT |  |  |  | 105°F AMBIENT |  |  |  | 115°F AMBIENT |  |  |  | 118.4°F AMBIENT |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg)
DHAC-020 | 21.5 | 20 | 51.6 | 10.9 | 20.2 | 22.2 | 48.4 | 9.2 | 18.4 | 24.6 | 44.1 | 8.1 | 17.9 | 25.6 | 42.9 | 6.7 | 17 | 27 | 40.4 | 6.8
DHAC-025 | 26.4 | 23.2 | 63.3 | 11.8 | 24.5 | 25.6 | 58.7 | 9.9 | 22.7 | 28.4 | 54.4 | 8.5 | 22.2 | 29.4 | 53.2 | 7.4 | 21 | 31.6 | 50 | 7.4
DHAC-030 | 31.8 | 31.8 | 76.5 | 16.6 | 29.5 | 35.6 | 70.7 | 15.5 | 27.5 | 39.6 | 65.9 | 12.7 | 26.7 | 41.2 | 64.2 | 12.9 | 24.9 | 44 | 59.6 | 6.4
DHAC-035 | 36.9 | 28.8 | 88.5 | 6.9 | 34.4 | 32 | 82.5 | 6 | 32.2 | 35.8 | 77.3 | 4.9 | 31 | 37.2 | 74.5 | 4.6 | 29.9 | 40 | 71.8 | 8
DHAC-040 | 42.6 | 36 | 102.2 | 9.7 | 39.8 | 40.2 | 95.5 | 7.6 | 37 | 45 | 88.8 | 6.7 | 36.3 | 46.8 | 87.1 | 6.9 | 34.2 | 51.2 | 82.2 | 7
DHAC-050 | 53 | 50.2 | 126.5 | 13.4 | 49.6 | 55.6 | 118.9 | 11.6 | 45.8 | 61.8 | 110 | 10.4 | 44.8 | 64.2 | 107.4 | 9.9 | 42 | 69.6 | 100.5 | 7
DHAC-060 | 67.4 | 65.7 | 153.8 | 19.4 | 64.6 | 72.5 | 155 | 12.6 | 56.8 | 82.3 | 131.7 | 14.1 | 55 | 84.5 | 132.5 | 9.7 | 52 | 90.3 | 125 | 6.5
DHAC-070 | 74.6 | 67.5 | 178.6 | 13.1 | 69.2 | 75.2 | 166 | 11.6 | 64.5 | 83.4 | 155 | 9.9 | 64 | 87.2 | 151.9 | 8.6 | 57.6 | 92.8 | 138.2 | 6.5
DHAC-075 | 79.8 | 74.7 | 202.7 | 8.3 | 79 | 83.7 | 190 | 7.6 | 72.5 | 93 | 174.1 | 6 | 70.7 | 97.2 | 169.7 | 5.8 | 65.7 | 103.2 | 160.5 | 7.2
DHAC-080 | 84.4 | 75.6 | 202.7 | 6.7 | 80.3 | 83.7 | 190 | 7.6 | 73.5 | 95.6 | 174.1 | 6 | 71.6 | 98.1 | 169.7 | 5.8 | 66.9 | 105 | 160.5 | 5.7
DHAC-095 | 100.4 | 101.1 | 241 | 6.5 | 93 | 111 | 224.8 | 8.3 | 86.6 | 121.9 | 207.6 | 6.7 | 84.4 | 125 | 202.5 | 6.9 | 79.2 | 133.5 | 190.1 | 6.7
DHAC-100 | 105.2 | 100.4 | 252.6 | 9.2 | 98.9 | 110.4 | 237.5 | 8.3 | 91.3 | 123.6 | 221.4 | 6.6 | 89.1 | 127.2 | 214 | 6.7 | 83.6 | 136.4 | 200.6 | 6.6

## LCWT 50F
DHAC Performance Data (English System) — Leaving Chilled Water Temp 50°F
UNIT SIZE | 95°F AMBIENT |  |  |  | 105°F AMBIENT |  |  |  | 115°F AMBIENT |  |  |  | 118.4°F AMBIENT |  |  |  | 125°F AMBIENT
| CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg) | CAP. (Tons) | COMP. POWER (kW) | WFR (GPM) | WPD (ft.wg)
DHAC-020 | 22.2 | 20.2 | 53.2 | 11.6 | 20.9 | 22.4 | 50 | 9.7 | 18.9 | 24.8 | 45.3 | 8.5 | 18.4 | 25.8 | 44.2 | 6.7 | 17.3 | 27.6 | 41.6 | 3.9
DHAC-025 | 27.2 | 23.4 | 65.3 | 11.6 | 25.4 | 25.8 | 60.5 | 10.4 | 23.6 | 28.6 | 56.1 | 9 | 22.8 | 29.6 | 54.8 | 8 | 21.7 | 31.8 | 52.1 | 7.9
DHAC-030 | 32.5 | 32 | 77.6 | 17.3 | 30.3 | 36.2 | 72.8 | 16.4 | 28.3 | 40.2 | 67.8 | 13.6 | 27.6 | 41.6 | 66.2 | 13.2 | 25.6 | 44.4 | 61.4 | 11.3
DHAC-035 | 38.1 | 29 | 91.5 | 7.6 | 35.8 | 32.2 | 85.9 | 6.5 | 33.3 | 36 | 79.5 | 5.5 | 32.5 | 37.4 | 77.6 | 4.9 | 31 | 40.2 | 74.2 | 4.4
DHAC-040 | 43.8 | 36.2 | 105.5 | 10.4 | 41 | 40.4 | 98.5 | 8.5 | 38 | 45.2 | 91.6 | 7.4 | 37 | 47 | 88.9 | 7 | 35 | 51.4 | 84.9 | 6
DHAC-050 | 54.2 | 50.8 | 130 | 14.1 | 50.7 | 56.2 | 121.6 | 12.6 | 46.9 | 62.2 | 112.6 | 11.1 | 45.8 | 64.6 | 110 | 10.4 | 43.5 | 68.4 | 104.8 | 9.5
DHAC-060 | 67.6 | 66 | 159 | 20.5 | 61.4 | 72.8 | 147.4 | 12.6 | 56.6 | 82.7 | 135.7 | 14.8 | 55 | 84.3 | 134.9 | 11.5 | 52.2 | 88.1 | 125.6 | 6.7
DHAC-070 | 76.7 | 68.1 | 184.1 | 13.9 | 70.7 | 75.8 | 170.7 | 12.4 | 65 | 83.6 | 156.2 | 11.8 | 65 | 87.2 | 156.1 | 9.6 | 61 | 93.5 | 146.2 | 7.6
DHAC-075 | 82.3 | 75.3 | 197.4 | 19 | 76.4 | 83.4 | 183.4 | 16.2 | 70.9 | 92.7 | 170.1 | 15.1 | 68.1 | 96.5 | 163.4 | 11 | 64.7 | 102.9 | 155.2 | 11.8
DHAC-080 | 87 | 76.2 | 208.8 | 9 | 81.7 | 84.3 | 196.1 | 8.1 | 74.6 | 93.6 | 179 | 6.2 | 73 | 98.1 | 174.7 | 6.6 | 68 | 106.2 | 163.5 | 6.2
DHAC-095 | 102.3 | 101.6 | 247.8 | 9.9 | 95.6 | 111 | 229.5 | 8.5 | 88.4 | 123 | 212.3 | 6.6 | 86 | 126.9 | 206 | 6.7 | 81.2 | 135.3 | 194.6 | 6.6
DHAC-100 | 108.2 | 101.6 | 259.7 | 9.7 | 102 | 111.2 | 244.8 | 8.8 | 95.3 | 124.8 | 228.8 | 6.9 | 92 | 129 | 220.7 | 7 | 86.9 | 137.2 | 206.5 | 6