## 3 Rows
NGW Performance Data — 3 Rows Cooling Coil
Model | Air Flow CFM | 42 °F |  |  |  | 43 °F |  |  |  | 44 °F |  |  |  | 45 °F |  |  |  | 46 °F |  |  |  | 47 °F |  |  |  | 48 °F
|  | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD
|  | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O
NGW-026 | 1800 | 67141 | 44415 | 13.43 | 7.1 | 63616 | 42669 | 12.72 | 6.44 | 60008 | 40880 | 12 | 5.79 | 56227 | 38995 | 11.25 | 5.13 | 52402 | 37077 | 10.48 | 4.52 | 48458 | 35078 | 9.69 | 3.93 | 44287 | 32923 | 8.86 | 3.34
| 2000 | 72056 | 47935 | 14.41 | 8.09 | 68252 | 46047 | 13.65 | 7.33 | 64327 | 44094 | 12.87 | 6.57 | 60282 | 42072 | 12.06 | 5.83 | 56167 | 40000 | 11.23 | 5.14 | 51897 | 37823 | 10.38 | 4.45 | 47456 | 35517 | 9.49 | 3.79
| 2200 | 76891 | 51409 | 15.38 | 9.07 | 72811 | 49381 | 14.56 | 8.22 | 68577 | 47267 | 13.72 | 7.35 | 64268 | 45107 | 12.85 | 6.53 | 59868 | 42883 | 11.97 | 5.75 | 55280 | 40531 | 11.06 | 4.97 | 50569 | 38074 | 10.11 | 4.24
| 2400 | 81646 | 54836 | 16.33 | 10.06 | 77295 | 52670 | 15.46 | 9.11 | 72759 | 50398 | 14.55 | 8.13 | 68186 | 48100 | 13.64 | 7.23 | 63505 | 45725 | 12.7 | 6.36 | 58607 | 43202 | 11.72 | 5.49 | 53626 | 40593 | 10.73 | 4.69
| 2600 | 86081 | 58075 | 17.22 | 11.04 | 81474 | 55777 | 16.29 | 9.99 | 76667 | 53363 | 15.33 | 8.92 | 71830 | 50923 | 14.37 | 7.92 | 66884 | 48406 | 13.38 | 6.97 | 61708 | 45727 | 12.34 | 6.02 | 56456 | 42962 | 11.29 | 5.13
| 3000 | 94222 | 64460 | 18.84 | 12.97 | 89094 | 61544 | 17.82 | 11.7 | 83881 | 58925 | 16.78 | 10.49 | 78546 | 56223 | 15.71 | 9.32 | 73053 | 53407 | 14.61 | 8.16 | 67435 | 50483 | 13.49 | 7.07 | 61622 | 47392 | 12.32 | 6.01
NGW-040 | 3200 | 119078 | 79468 | 23.82 | 6.4 | 113297 | 76530 | 22.66 | 5.8 | 107312 | 73686 | 21.46 | 5.19 | 99281 | 69574 | 19.86 | 4.6 | 92263 | 66016 | 18.45 | 4.03 | 85030 | 62299 | 17.01 | 3.47 | 77441 | 58317 | 15.49 | 2.93
| 3500 | 126519 | 84838 | 25.3 | 7.14 | 120109 | 81669 | 24.02 | 6.45 | 113036 | 78167 | 22.62 | 5.78 | 105384 | 74246 | 21.08 | 5.12 | 97916 | 70445 | 19.58 | 4.48 | 90235 | 66482 | 18.05 | 3.87 | 82210 | 62252 | 16.44 | 3.27
| 3700 | 131479 | 88418 | 26.3 | 7.64 | 124650 | 85028 | 24.93 | 6.89 | 116969 | 81154 | 23.39 | 6.17 | 109453 | 77360 | 21.89 | 5.47 | 101685 | 73397 | 20.34 | 4.78 | 93705 | 69270 | 18.74 | 4.13 | 85389 | 64875 | 17.08 | 3.49
| 4000 | 138336 | 93444 | 27.67 | 8.37 | 130946 | 89755 | 26.19 | 7.54 | 123514 | 86043 | 24.7 | 6.75 | 115080 | 81738 | 23.02 | 5.99 | 106891 | 77543 | 21.38 | 5.05 | 98490 | 73179 | 19.7 | 4.51 | 89746 | 68536 | 17.95 | 3.81
| 4200 | 142908 | 96794 | 28.58 | 8.86 | 135143 | 92906 | 27.03 | 7.98 | 127878 | 89303 | 25.58 | 7.14 | 118832 | 84656 | 23.77 | 6.33 | 110846 | 80307 | 22.07 | 5.23 | 101680 | 75795 | 20.34 | 4.77 | 92650 | 70976 | 18.53 | 4.03
NGW-050 | 4400 | 148723 | 100844 | 29.74 | 3.55 | 140359 | 96634 | 28.07 | 3.2 | 131800 | 92303 | 26.36 | 2.85 | 122954 | 87783 | 24.59 | 2.51 | 113912 | 83111 | 22.78 | 2.05 | 104514 | 78164 | 20.9 | 1.88 | 94772 | 72914 | 18.95 | 1.57
| 4700 | 155142 | 105602 | 31.03 | 3.83 | 146387 | 101185 | 29.28 | 3.45 | 137435 | 96643 | 27.49 | 3.08 | 128185 | 91902 | 25.64 | 2.71 | 118740 | 87004 | 23.75 | 2.29 | 108934 | 81822 | 21.79 | 2.03 | 98780 | 76326 | 19.76 | 1.7
| 5000 | 161561 | 110360 | 32.31 | 4.11 | 152415 | 105736 | 30.48 | 3.7 | 143069 | 100983 | 28.61 | 3.3 | 133415 | 96020 | 26.68 | 2.9 | 123568 | 90897 | 24.71 | 2.53 | 113353 | 85480 | 22.67 | 2.17 | 102788 | 79737 | 20.56 | 1.82
| 5300 | 167194 | 114636 | 33.44 | 4.62 | 157700 | 109825 | 31.54 | 3.94 | 147974 | 104861 | 29.59 | 3.51 | 138273 | 99710 | 27.65 | 3.09 | 127778 | 94380 | 25.56 | 2.68 | 117197 | 88744 | 23.44 | 2.31 | 106264 | 82776 | 21.25 | 1.93
| 5600 | 173220 | 119154 | 34.64 | 5.02 | 163357 | 114145 | 32.67 | 4.19 | 153243 | 108970 | 30.65 | 3.73 | 143317 | 103615 | 28.66 | 3.28 | 132297 | 98068 | 26.46 | 2.87 | 121329 | 92205 | 24.27 | 2.45 | 110005 | 86001 | 22 | 2.2
| 6000 | 180993 | 125016 | 36.2 | 4.68 | 170652 | 119751 | 34.13 | 4.51 | 160026 | 114295 | 32.01 | 4.01 | 149918 | 108678 | 29.98 | 3.54 | 138117 | 102849 | 27.62 | 3.1 | 126646 | 96689 | 25.33 | 2.63 | 114817 | 90177 | 22.96 | 2.2
NGW-080 | 6200 | 228293 | 152622 | 45.66 | 13.3 | 216816 | 146958 | 43.36 | 12.11 | 205104 | 141174 | 41.02 | 10.95 | 193124 | 135240 | 38.62 | 9.82 | 180799 | 129023 | 36.16 | 8.7 | 168218 | 122767 | 33.64 | 7.64 | 155235 | 116146 | 31.05 | 6.61
| 6500 | 235328 | 157762 | 47.07 | 14.05 | 223457 | 151896 | 44.69 | 12.78 | 211343 | 145905 | 42.27 | 11.59 | 198959 | 139760 | 39.79 | 10.36 | 186186 | 133347 | 37.24 | 9.18 | 173217 | 126836 | 34.64 | 8.05 | 159806 | 119976 | 31.96 | 6.96
| 7000 | 247053 | 166328 | 49.41 | 15.29 | 234524 | 160127 | 46.9 | 13.9 | 221741 | 153790 | 44.35 | 12.66 | 208683 | 147292 | 41.74 | 11.25 | 195249 | 140554 | 39.05 | 9.97 | 181548 | 133617 | 36.31 | 8.74 | 167425 | 126358 | 33.49 | 7.55
| 7500 | 257751 | 174278 | 51.55 | 16.51 | 244614 | 167764 | 48.92 | 15.01 | 231219 | 161106 | 46.24 | 13.61 | 217505 | 154257 | 43.5 | 12.12 | 203463 | 147190 | 40.69 | 10.74 | 189122 | 139896 | 37.82 | 9.41 | 174341 | 132259 | 34.87 | 8.13
| 8000 | 268448 | 182229 | 53.69 | 17.73 | 254705 | 175401 | 50.94 | 16.11 | 240697 | 168422 | 48.14 | 14.57 | 226327 | 161221 | 45.27 | 12.99 | 211677 | 153825 | 42.34 | 11.51 | 196695 | 146176 | 39.34 | 10.08 | 181257 | 138161 | 36.25 | 8.7
| 8400 | 277006 | 188589 | 55.4 | 18.7 | 262777 | 181510 | 52.56 | 17 | 248279 | 174275 | 49.66 | 15.33 | 233384 | 166793 | 46.68 | 13.69 | 218249 | 159134 | 43.65 | 12.13 | 202754 | 151199 | 40.55 | 10.62 | 186790 | 142882 | 37.36 | 9.16
NGW-100 | 8600 | 280297 | 192568 | 56.54 | 12.41 | 268317 | 185417 | 53.66 | 11.29 | 253641 | 178104 | 50.73 | 10.2 | 238554 | 170537 | 47.71 | 9.11 | 223203 | 162777 | 44.64 | 8.11 | 207476 | 154734 | 41.5 | 7.08 | 191249 | 146291 | 38.25 | 6.11
| 9000 | 290576 | 198499 | 58.12 | 13.04 | 275743 | 191117 | 55.15 | 11.86 | 260619 | 183565 | 52.12 | 10.71 | 245069 | 175149 | 49.01 | 9.56 | 229258 | 167734 | 45.85 | 8.5 | 213063 | 159427 | 42.61 | 7.43 | 196356 | 150704 | 39.27 | 6.41
| 9500 | 300411 | 205912 | 60.08 | 13.83 | 285025 | 198242 | 57 | 12.57 | 269342 | 190392 | 53.87 | 11.34 | 253214 | 182260 | 50.64 | 10.13 | 236828 | 173931 | 47.37 | 8.99 | 220046 | 165292 | 44.01 | 7.86 | 202741 | 156221 | 40.55 | 6.79
| 10000 | 310247 | 213326 | 62.05 | 14.62 | 294307 | 205367 | 58.86 | 13.28 | 278064 | 197219 | 55.61 | 11.98 | 261358 | 188773 | 52.27 | 10.7 | 244397 | 180128 | 48.88 | 9.48 | 227030 | 171158 | 45.41 | 8.3 | 209125 | 161738 | 41.83 | 7.16
| 10500 | 319351 | 220283 | 63.87 | 15.4 | 302897 | 212050 | 60.58 | 13.98 | 286058 | 203592 | 57.22 | 12.6 | 268887 | 194880 | 53.78 | 11.25 | 251389 | 185934 | 50.28 | 9.97 | 233433 | 176544 | 46.69 | 8.72 | 215016 | 166903 | 43 | 7.52
| 11000 | 328455 | 227240 | 65.69 | 16.17 | 311487 | 218733 | 62.3 | 14.68 | 294095 | 209964 | 58.82 | 13.21 | 276415 | 200987 | 55.28 | 11.83 | 258380 | 191740 | 51.68 | 10.46 | 239836 | 182090 | 47.97 | 9.14 | 220906 | 172067 | 44.18 | 7.88

## 4 Rows
NGW Performance Data — 4 Rows Cooling Coil
Model | Air Flow CFM | 42 °F |  |  |  | 43 °F |  |  |  | 44 °F |  |  |  | 45 °F |  |  |  | 46 °F |  |  |  | 47 °F |  |  |  | 48 °F
|  | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD | Total Capacity | Sensible Capacity | Water Flow | WPD
|  | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O | Btu/hr | Btu/hr | GPM | Ft H2O
NGW-026 | 1800 | 79626 | 51641 | 15.93 | 5.8 | 75602 | 49654 | 15.12 | 5.2 | 71436 | 47603 | 14.3 | 4.7 | 67166 | 45501 | 13.43 | 4.2 | 62736 | 43313 | 12.55 | 3.7 | 58158 | 41037 | 11.63 | 3.3 | 53359 | 38619 | 10.67 | 2.8
| 2000 | 85871 | 55960 | 17.17 | 6.63 | 81498 | 53800 | 16.3 | 6 | 76988 | 51577 | 15.4 | 5.4 | 72363 | 49296 | 14.47 | 4.83 | 67568 | 46921 | 13.51 | 4.27 | 62625 | 44455 | 12.53 | 3.77 | 57455 | 41839 | 11.49 | 3.2
| 2200 | 92116 | 60280 | 18.42 | 7.47 | 87393 | 57947 | 17.48 | 6.8 | 82540 | 55552 | 16.5 | 6.1 | 77559 | 53091 | 15.51 | 5.47 | 72399 | 50529 | 14.48 | 4.83 | 67092 | 47874 | 13.42 | 4.23 | 61506 | 45060 | 12.31 | 3.6
| 2400 | 98361 | 64599 | 19.67 | 8.3 | 93289 | 62093 | 18.66 | 7.6 | 88092 | 59526 | 17.6 | 6.8 | 82756 | 56886 | 16.55 | 6.13 | 77231 | 54137 | 15.45 | 5.4 | 71559 | 51292 | 14.31 | 4.7 | 65646 | 48280 | 13.13 | 4
| 2600 | 103852 | 68492 | 20.77 | 9.2 | 98467 | 65828 | 19.69 | 8.4 | 92953 | 63100 | 18.6 | 7.5 | 87281 | 60287 | 17.46 | 6.73 | 81441 | 57372 | 16.29 | 5.93 | 75426 | 54343 | 15.09 | 5.17 | 69189 | 51154 | 13.84 | 4.4
| 3000 | 114834 | 76278 | 22.97 | 11 | 108823 | 73299 | 21.76 | 10 | 102675 | 70249 | 20.5 | 8.9 | 96332 | 67088 | 19.27 | 8 | 89860 | 63843 | 17.97 | 7 | 83160 | 60446 | 16.63 | 6.1 | 76275 | 56902 | 15.26 | 5.2
NGW-040 | 3200 | 137235 | 89799 | 27.57 | 4.7 | 130615 | 86208 | 26.12 | 4.2 | 123157 | 82519 | 24.6 | 3.8 | 115416 | 78681 | 23.08 | 3.4 | 107447 | 74712 | 21.49 | 3 | 99107 | 70513 | 19.82 | 2.6 | 90367 | 66043 | 18.07 | 2.2
| 3500 | 147234 | 96278 | 29.45 | 5.3 | 139454 | 92422 | 27.89 | 4.74 | 131460 | 88464 | 26.3 | 4.28 | 123170 | 84347 | 24.63 | 3.82 | 114653 | 80095 | 22.93 | 3.36 | 105758 | 75606 | 21.15 | 2.9 | 96465 | 70838 | 19.29 | 2.44
| 3700 | 153480 | 100597 | 30.7 | 5.7 | 145346 | 96565 | 29.07 | 5.1 | 136995 | 92427 | 27.4 | 4.6 | 128339 | 88124 | 25.67 | 4.1 | 119457 | 83684 | 23.89 | 3.6 | 110192 | 79001 | 22.04 | 3.1 | 100531 | 74034 | 20.11 | 2.6
| 4000 | 162223 | 106724 | 32.44 | 6.24 | 153585 | 102438 | 30.72 | 5.64 | 144727 | 98044 | 28.9 | 5.08 | 135548 | 93471 | 27.11 | 4.52 | 126145 | 88760 | 25.23 | 3.96 | 116347 | 83792 | 23.27 | 3.4 | 106157 | 78535 | 21.23 | 2.9
| 4200 | 168051 | 110808 | 33.61 | 6.6 | 159077 | 106354 | 31.82 | 6 | 149881 | 101788 | 30 | 5.4 | 140354 | 97036 | 28.07 | 4.8 | 130604 | 92144 | 26.12 | 4.2 | 120451 | 86986 | 24.09 | 3.6 | 109907 | 81536 | 21.98 | 3.1
NGW-050 | 4400 | 184227 | 120564 | 36.85 | 20.1 | 175545 | 116319 | 35.11 | 18.4 | 166676 | 111995 | 33.3 | 16.8 | 157598 | 107575 | 31.52 | 15.1 | 148253 | 103017 | 29.65 | 13.5 | 138706 | 98347 | 27.74 | 12 | 128900 | 93515 | 25.78 | 10.5
| 4700 | 192730 | 126561 | 38.55 | 21.8 | 183597 | 122094 | 36.72 | 19.95 | 174271 | 117543 | 34.9 | 18.15 | 164699 | 112873 | 32.94 | 16.35 | 154904 | 108088 | 30.98 | 14.65 | 144881 | 103169 | 28.98 | 12.95 | 134553 | 98062 | 26.91 | 11.35
| 5000 | 201233 | 132558 | 40.25 | 23.5 | 191649 | 127868 | 38.33 | 21.5 | 181865 | 123090 | 36.4 | 19.5 | 171800 | 118171 | 34.36 | 17.6 | 161554 | 113158 | 32.31 | 15.8 | 151056 | 107991 | 30.21 | 13.9 | 140205 | 102609 | 28.04 | 12.2
| 5300 | 208809 | 138245 | 41.76 | 16.51 | 198816 | 133129 | 39.76 | 23.02 | 188591 | 128126 | 37.7 | 20.89 | 178132 | 123008 | 35.63 | 18.82 | 167451 | 117768 | 33.49 | 16.86 | 156516 | 112374 | 31.3 | 14.9 | 145253 | 106755 | 29.05 | 13.04
| 5600 | 216849 | 143755 | 43.37 | 25.02 | 206425 | 138647 | 41.29 | 24.56 | 195751 | 133418 | 39.2 | 22.26 | 184849 | 128056 | 36.97 | 20.06 | 173724 | 122609 | 34.74 | 17.96 | 162334 | 116977 | 32.47 | 15.88 | 150573 | 111101 | 30.11 | 13.88
| 6000 | 227260 | 151220 | 45.49 | 29.1 | 216276 | 145833 | 43.26 | 26.6 | 205008 | 140304 | 41 | 24.1 | 193548 | 134679 | 38.71 | 21.7 | 181838 | 128909 | 36.37 | 19.4 | 169853 | 122967 | 33.97 | 17.2 | 157485 | 116763 | 31.5 | 15
NGW-080 | 6200 | 246736 | 162837 | 49.35 | 8.8 | 234430 | 156779 | 46.89 | 8 | 221907 | 150622 | 44.4 | 7.3 | 209079 | 144309 | 41.82 | 6.5 | 195942 | 137819 | 39.19 | 5.8 | 182361 | 131056 | 36.47 | 5.1 | 168451 | 124054 | 33.69 | 4.4
| 6500 | 254671 | 168506 | 50.93 | 9.32 | 241944 | 162237 | 48.39 | 8.49 | 228973 | 155854 | 45.8 | 7.71 | 208931 | 149308 | 41.79 | 6.88 | 202065 | 142562 | 40.41 | 6.14 | 188040 | 135564 | 37.61 | 5.4 | 173656 | 128304 | 34.73 | 4.63
| 7000 | 267895 | 177953 | 53.58 | 10.2 | 254466 | 171334 | 50.89 | 9.3 | 240750 | 164575 | 48.2 | 8.4 | 220683 | 157640 | 41.74 | 7.5 | 212271 | 150467 | 42.45 | 6.7 | 197504 | 143076 | 39.5 | 5.9 | 182331 | 135386 | 36.47 | 5
| 7500 | 280058 | 186781 | 56.01 | 11.06 | 265947 | 179871 | 53.19 | 10.09 | 251537 | 172701 | 50.3 | 9.08 | 225208 | 165402 | 45.04 | 8.14 | 221637 | 157847 | 44.33 | 7.24 | 206147 | 150063 | 41.23 | 6.36 | 190210 | 141947 | 38.04 | 5.43
| 8000 | 292221 | 195609 | 58.44 | 11.91 | 277427 | 188299 | 55.49 | 10.87 | 262324 | 180827 | 52.5 | 9.76 | 241733 | 173164 | 48.35 | 8.79 | 231004 | 165227 | 46.2 | 7.77 | 214789 | 157050 | 42.96 | 6.83 | 198089 | 148509 | 39.62 | 5.86
| 8400 | 299481 | 202671 | 60.39 | 12.6 | 286612 | 195085 | 57.32 | 11.5 | 270954 | 187328 | 54.2 | 10.3 | 254953 | 179738 | 50.99 | 9.3 | 238497 | 171131 | 47.7 | 8.2 | 221703 | 162640 | 44.34 | 7.2 | 204392 | 153758 | 40.88 | 6.2
NGW-100 | 8600 | 335671 | 222244 | 67.13 | 9.5 | 318847 | 213957 | 63.77 | 8.7 | 301733 | 205534 | 60.3 | 7.8 | 284148 | 196858 | 56.83 | 7 | 266289 | 188022 | 53.26 | 6.2 | 247747 | 178759 | 49.55 | 5.5 | 228780 | 169181 | 45.76 | 4.7
| 9000 | 345811 | 229547 | 69.16 | 10.01 | 328445 | 220988 | 65.69 | 9.16 | 310756 | 212272 | 62.2 | 8.23 | 292606 | 203305 | 58.52 | 7.4 | 274102 | 194128 | 54.82 | 6.54 | 254987 | 184559 | 51 | 5.79 | 235479 | 174627 | 47.1 | 4.96
| 9500 | 358487 | 238677 | 71.7 | 10.66 | 340443 | 229776 | 68.09 | 9.73 | 322034 | 220694 | 64.4 | 8.76 | 303179 | 211364 | 60.64 | 7.9 | 283868 | 201760 | 56.77 | 6.97 | 264037 | 191809 | 52.81 | 6.14 | 243815 | 181435 | 48.76 | 5.28
| 10000 | 371162 | 247806 | 74.23 | 11.3 | 352440 | 238565 | 71.4 | 10.3 | 333312 | 229116 | 66.7 | 9.3 | 313752 | 219423 | 62.75 | 8.4 | 293634 | 209392 | 58.73 | 7.4 | 273087 | 199059 | 54.62 | 6.5 | 252151 | 188243 | 50.43 | 5.6
| 10500 | 383008 | 256448 | 76.6 | 11.95 | 363612 | 246864 | 72.72 | 10.9 | 343868 | 237068 | 68 | 9.85 | 323566 | 227017 | 64.71 | 8.9 | 302743 | 216610 | 60.55 | 7.8 | 281494 | 205894 | 56.3 | 6.85 | 260487 | 194670 | 52.1 | 5.9
| 11000 | 394853 | 265090 | 78.97 | 12.6 | 374784 | 255162 | 74.96 | 11.5 | 354308 | 245019 | 70.9 | 10.4 | 333379 | 234611 | 66.68 | 9.3 | 311852 | 223827 | 62.37 | 8.2 | 289900 | 212729 | 57.98 | 7.2 | 267243 | 201098 | 53.45 | 6.2