## Fan Performance (4 Rows)
FAN PERFORMANCE (4 ROWS)
Model | CFM | External Static Pressure [in.wg]
|  | 0.40 |  | 0.70 |  | 1.00 |  | 1.25 |  | 1.50 |  | 1.75 |  | 2.00
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
SPU-420 | 10500 | 662 | 3.81 | 733 | 4.61 | 802 | 5.5 | 858 | 6.31 | 914 | 7.21 | 970 | 8.19 | 1025 | 9.25
| 11400 | 670 | 4.29 | 738 | 5.11 | 803 | 6 | 856 | 6.79 | 908 | 7.67 | 960 | 8.59 | 1011 | 9.6
| 12300 | 680 | 4.84 | 745 | 4.24 | 807 | 6.58 | 857 | 7.39 | 907 | 8.23 | 955 | 9.14 | 1003 | 10.11
| 13200 | 691 | 5.47 | 754 | 6.33 | 813 | 7.25 | 862 | 8.06 | 909 | 8.91 | 955 | 9.81 | 1000 | 10.75
SPU-480 | 12000 | 676 | 4.65 | 742 | 5.48 | 805 | 6.38 | 856 | 7.17 | 907 | 8.05 | 956 | 8.94 | 1005 | 9.92
| 13000 | 688 | 5.32 | 752 | 6.18 | 812 | 7.09 | 860 | 7.9 | 908 | 8.75 | 955 | 9.65 | 1001 | 10.6
| 14000 | 701 | 6.07 | 763 | 6.97 | 821 | 7.91 | 867 | 8.74 | 913 | 9.6 | 957 | 10.5 | 1001 | 11.45
| 15000 | 716 | 6.9 | 775 | 7.86 | 832 | 8.83 | 877 | 9.68 | 920 | 10.55 | 963 | 11.46 | 1005 | 12.41
SPU-540 | 13500 | 653 | 4.89 | 719 | 5.79 | 784 | 6.77 | 837 | 7.64 | 889 | 8.58 | 940 | 9.56 | 990 | 10.59
| 14600 | 663 | 5.56 | 726 | 6.49 | 787 | 7.48 | 837 | 8.36 | 886 | 9.29 | 934 | 10.28 | 982 | 11.31
| 15700 | 675 | 6.31 | 736 | 7.28 | 793 | 8.3 | 841 | 9.18 | 887 | 10.12 | 933 | 11.11 | 978 | 12.14
| 16800 | 689 | 7.17 | 747 | 8.16 | 802 | 9.21 | 847 | 10.12 | 891 | 11.07 | 935 | 12.06 | 978 | 13.1
SPU-600 | 15000 | 668 | 5.83 | 729 | 6.75 | 789 | 7.76 | 838 | 8.65 | 886 | 9.58 | 933 | 10.56 | 980 | 11.6
| 16100 | 680 | 6.62 | 739 | 7.59 | 796 | 8.61 | 843 | 9.5 | 888 | 10.46 | 933 | 11.45 | 977 | 12.48
| 17200 | 694 | 7.49 | 751 | 8.51 | 806 | 9.57 | 850 | 10.48 | 893 | 11.45 | 936 | 12.44 | 978 | 13.47
| 18300 | 708 | 8.47 | 764 | 9.53 | 817 | 10.63 | 859 | 11.57 | 901 | 12.55 | 942 | 13.55 | 982 | 14.61
SPU-660 | 16500 | 394 | 5.51 | 435 | 6.54 | 474 | 7.67 | 507 | 8.67 | 538 | 9.75 | 569 | 10.87 | 600 | 12.06
| 17700 | 400 | 6.17 | 438 | 7.22 | 476 | 8.36 | 506 | 9.37 | 536 | 10.44 | 566 | 11.57 | 595 | 12.76
| 19000 | 406 | 6.97 | 443 | 8.07 | 479 | 9.22 | 508 | 10.24 | 536 | 11.31 | 564 | 12.45 | 592 | 13.63
| 20300 | 414 | 7.86 | 449 | 9 | 483 | 10.19 | 511 | 11.22 | 538 | 12.31 | 565 | 13.44 | 591 | 14.64
SPU-720 | 18000 | 401 | 6.35 | 439 | 7.41 | 476 | 8.55 | 509 | 9.56 | 536 | 10.63 | 565 | 11.77 | 594 | 12.95
| 19400 | 408 | 7.24 | 445 | 8.38 | 480 | 9.5 | 509 | 10.54 | 537 | 11.61 | 564 | 12.75 | 592 | 13.93
| 20800 | 417 | 8.24 | 452 | 9.4 | 485 | 10.59 | 513 | 11.64 | 539 | 12.72 | 566 | 13.87 | 592 | 15.05
| 22200 | 425 | 9.36 | 460 | 10.56 | 492 | 11.8 | 518 | 12.87 | 543 | 13.98 | 569 | 15.15 | 593 | 16.34
FAN PERFORMANCE (4 ROWS)
Model | CFM | External Static Pressure [in.wg]
|  | 0.40 |  | 0.70 |  | 1.00 |  | 1.25 |  | 1.50 |  | 1.75 |  | 2.00
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
SPU-780 | 19500 | 347 | 6.3 | 385 | 7.59 | 422 | 9.02 | 452 | 10.29 | 482 | 11.66 | 510 | 13.08 | 538 | 14.58
| 21000 | 351 | 7.04 | 387 | 8.35 | 421 | 9.79 | 450 | 11.06 | 478 | 12.43 | 506 | 13.86 | 533 | 15.36
| 22500 | 355 | 7.87 | 389 | 9.21 | 423 | 10.66 | 450 | 11.94 | 477 | 13.31 | 503 | 14.75 | 529 | 16.26
| 24000 | 361 | 8.81 | 394 | 10.19 | 425 | 11.65 | 451 | 12.95 | 477 | 14.32 | 502 | 15.75 | 527 | 17.27
SPU-840 | 21000 | 351 | 7.04 | 387 | 8.35 | 421 | 9.79 | 450 | 11.06 | 478 | 12.43 | 506 | 13.86 | 533 | 15.36
| 22500 | 355 | 7.87 | 389 | 9.21 | 423 | 10.66 | 450 | 11.94 | 477 | 13.31 | 503 | 14.75 | 529 | 16.26
| 24000 | 361 | 8.81 | 394 | 10.19 | 425 | 11.65 | 451 | 12.95 | 477 | 14.32 | 502 | 15.75 | 527 | 17.27
| 25500 | 367 | 9.83 | 398 | 11.26 | 429 | 12.76 | 454 | 14.08 | 478 | 15.44 | 502 | 16.89 | 526 | 18.4
SPU-960 | 24000 | 361 | 8.81 | 394 | 10.19 | 425 | 11.65 | 451 | 12.95 | 477 | 14.32 | 502 | 15.75 | 527 | 17.27
| 25600 | 367 | 9.91 | 398 | 11.33 | 429 | 12.83 | 454 | 14.14 | 478 | 15.5 | 501 | 16.97 | 526 | 18.49
| 27200 | 374 | 11.11 | 405 | 12.6 | 434 | 14.14 | 458 | 15.5 | 481 | 16.89 | 504 | 18.35 | 526 | 19.87
| 28800 | 381 | 12.44 | 411 | 13.99 | 440 | 15.6 | 462 | 16.97 | 485 | 18.39 | 507 | 19.88 | 528 | 21.41
SPU-1080 | 27000 | 313 | 9.14 | 344 | 10.82 | 375 | 12.63 | 400 | 14.25 | 425 | 15.98 | 449 | 17.79 | 475 | 19.69
| 28800 | 317 | 10.17 | 347 | 11.88 | 376 | 13.71 | 400 | 15.34 | 424 | 17.06 | 447 | 18.88 | 470 | 20.79
| 30600 | 322 | 13.31 | 351 | 13.07 | 379 | 14.92 | 402 | 16.57 | 424 | 18.3 | 446 | 20.24 | 468 | 22.04
| 32400 | 327 | 12.56 | 355 | 14.37 | 382 | 16.27 | 404 | 17.94 | 425 | 19.68 | 447 | 21.51 | 468 | 23.42
SPU-1200 | 30000 | 320 | 10.92 | 349 | 12.65 | 378 | 14.5 | 401 | 16.14 | 424 | 17.87 | 446 | 19.69 | 469 | 21.6
| 32000 | 326 | 12.27 | 354 | 14.04 | 381 | 15.95 | 403 | 17.61 | 425 | 19.36 | 446 | 21.19 | 468 | 23.1
| 34000 | 332 | 13.77 | 359 | 12.56 | 385 | 17.57 | 406 | 19.29 | 427 | 21.03 | 448 | 22.87 | 468 | 24.79
| 36000 | 338 | 15.4 | 365 | 17.35 | 390 | 19.36 | 411 | 21.09 | 431 | 22.88 | 450 | 24.75 | 470 | 26.68
LEGEND:
RPM |  | Fan Speed in revolution per minute
BHP |  | Fan absorbed power
Note:
1. |  | Internal Static pressure is based on pressure drops through evaporator coil, fan casing and 2" washable filters.
2. |  | Blue shaded area indicates the operating range of a standard motor and drive combination.
3. |  | Green shaded area indicates the operating range of a standard motor with non standard drive combination.
4. |  | Gray shaded area indicates operating range using non standard motor and drive combination.
5. |  | To determine the power of motor to be installed, just multiply the value of the absorbed power indicated above by 1.2.