## Submittal
PRODUCT SUBMITTAL
Fresh Air Package Unit
Project Name : |  | Test Project |  |  | Unit Model : |  | FAPU-180F2T
Reference No. : |  | UA19-001-00 |  |  | Tag No. : |  | FAPU-1
Revision No. : |  | 0 |  |  | Sales Engineer : |  | 0
Date |  | 2026-06-29 |  |  | Prepared by : |  | 0
PERFORMANCE DATA
Unit Model |  | FAPU-180F2T |  | Qty |  | 1
Entering Air Temp (DB) |  | 118.4 | °F | Power Supply |  | 400V/3Ø/50Hz
Entering Air Temp (WB) |  | 80 | °F | Refrigerant |  | R410A
Altitude |  | 0 | Ft | ESP |  | 1 | In WG
Total Cooling Capacity |  | 149718.1808 | Btu/hr | Electric Heater |  | 0 | KW
Sensible Capacity |  | 123560.0369 | Btu/hr | Total Power Input |  | 20.1339 | KW
Air Flow |  | 1900 | CFM | Unit MCA |  | 44.725 | A
Face Velocity |  | 316.6667 | FPM | Unit MOCP |  | 50 | A
Leaving Air DB |  | 58.1856 | °F | EER |  | 7.4361
Leaving Air WB |  | 58.1856 | °F
TECHNICAL DATA
Compressor
Type |  | Hermetic Scroll |  | Refrigerant circuit |  | 2
Qty (Comp1)/(Comp2) |  | 2 | - | Capacity Step |  | 0-50-100
Size-HP (Comp1)/(Comp2) |  | 7.5833 | -
Condenser & Fan Motor Assy.
Rows |  | 3 |  | No. of Condenser Coil |  | 2
Fins per inch |  | 16
Face Area (ft²) |  | 33.3333 |  | Condenser Motor (HP) |  | 1.5
Coil Type |  | 3/8" Ø IGT Copper |  | No. of fans |  | 2
Fin Type |  | Aluminum
Fan type |  | Direct driven Propeller fan
Fan Motor |  | TEAO with Class F motor insulation with inherent thermal protection
Evaporator
Rows |  | 5 |  | Blower Motor (KW) |  | 3
Fins per inch |  | 12 |  | No. of fans |  | 1
Face Area (ft²) |  | 6
Coil Type |  | 3/8" Ø IGT Copper
Fin Type |  | Aluminum
Blower type |  | DWDI Backward curve centrifugal fan
Blower Motor |  | Totally Enclosed Fan Cooled (TEFC) type, IP 55 Protected, 2 Pole class F insulation
Drive type |  | Belt driven with adjustable motor pulley
Casing |  | Single skin construction with 15 mm thick fiberglass insulation
Pre Filter |  | 2" Aluminum washable
Final Filter |  | High efficiency synthetic bag filter
ADDITIONAL OPTIONS
- Compressor circuit breaker
- Manual High & Low pressure switch
- Rotalock valve for compressor
- Pump down kit
- Double skin Evaporator casing
UNIT LAYOUT
Model : | FAPU-180F2T
3
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
Entering Enthalpy |  | 43.1553
Leaving Enthalpy |  | 25.6444
[11 empty] | C8 | C9 | C10 | C11 | C12 | C13 | C14 | C15 | C16 | C17 | C18
[9 empty] | P = Barometric Pressure, in. Hg | 29.921 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546 | 100.45 | 33.193 | 2.319 | 0.17074 | 1.2063
[9 empty] | P (psia) | 14.6958
[9 empty] | T = Absolute temperature at dry-bulb temperature (t), °R | 578.07
[9 empty] | T* = Absolute temperature at wet-bulb temperature (t*), °R | 539.67
[9 empty] | Pws = Pressure of saturated pure water at dry-bulb Temperature (Psia) (for t = 32 to 392 °F) | 1.6208
[9 empty] | P*ws = Pressure of saturated pure water at wet-bulb Temperature (Psia) (for t* = 32 to 392 °F) | 0.50735
[9 empty] | Ws= Humidity ratio of moist air at saturation at dry-bulb temperature. lb (water)/lb (dry air) | 0.077102
[9 empty] | Ws*= Humidity ratio of moist air at saturation at wet-bulb temperature. lb (water)/lb (dry air) | 0.022241
[9 empty] | W= Humidity Ratio of Moist Air. lb(water)/lb(dry air) | 0.013236
[9 empty] | μ=Degree of Saturation | 0.17167
[9 empty] | Pw = Water Vapor Partial Pressure, psia | 0.30622
[9 empty] | α | -1.1835
[11 empty] | C8 | C9 | C10 | C11 | C12 | C13
[9 empty] | P2 = Barometric Pressure, in. Hg | 29.921 | C8: -10440.397; C9: -11.2947; C10: -0.027022; C11: 1.289e-05; C12: -2.4781e-09; C13: 6.546
[9 empty] | P2 (psia) | 14.6958
[9 empty] | T2 = Absolute temperature at dry-bulb temperature (t), °R | 517.8556
[9 empty] | T*2 = Absolute temperature at wet-bulb temperature (t*), °R | 517.8556
[9 empty] | Pws2 = Pressure of saturated pure water at dry-bulb Temperature (Psia) (for t = 32 to 392 °F) | 0.24024
[9 empty] | P*ws2 = Pressure of saturated pure water at wet-bulb Temperature (Psia) (for t* = 32 to 392 °F) | 0.24024
[9 empty] | Ws2= Humidity ratio of moist air at saturation at dry-bulb temperature. lb (water)/lb (dry air) | 0.010337
[9 empty] | Ws*2= Humidity ratio of moist air at saturation at wet-bulb temperature. lb (water)/lb (dry air) | 0.010337
[9 empty] | W2= Humidity Ratio of Moist Air. lb(water)/lb(dry air) | 0.010749
[9 empty] | μ2=Degree of Saturation | 1.0399
[9 empty] | Pw = Water Vapor Partial Pressure, psia | 0.24966
[9 empty] | α | -1.3877
[11 empty] | WB | 58.6
[11 empty] | W | h | Ref h
[9 empty] | DB | Pws* | 0.0011103 | 10.8067 | 25.6444 |  |  |  |  | Ratio | Round off | WB | P(psia) | C8 | C9 | C10 | C11 | C12 | C13
[9 empty] | 58.1856 | 0.12172 | 0.0011527 | 10.8768 | 25.6444 |  |  |  |  | 0.42141 | 0.421 | 40 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1222 | 0.0011951 | 10.9469 | 25.6444 |  |  |  |  | 0.42414 | 0.424 | 40.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12267 | 0.0012376 | 11.0171 | 25.6444 |  |  |  |  | 0.42687 | 0.427 | 40.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12315 | 0.0012802 | 11.0874 | 25.6444 |  |  |  |  | 0.42961 | 0.43 | 40.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12363 | 0.0013229 | 11.1577 | 25.6444 |  |  |  |  | 0.43235 | 0.432 | 40.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12411 | 0.0013656 | 11.2282 | 25.6444 |  |  |  |  | 0.43509 | 0.435 | 40.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1246 | 0.0014084 | 11.2987 | 25.6444 |  |  |  |  | 0.43784 | 0.438 | 40.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12508 | 0.0014513 | 11.3694 | 25.6444 |  |  |  |  | 0.44059 | 0.441 | 40.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12557 | 0.0014943 | 11.4401 | 25.6444 |  |  |  |  | 0.44335 | 0.443 | 40.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12605 | 0.0015374 | 11.5109 | 25.6444 |  |  |  |  | 0.4461 | 0.446 | 40.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12654 | 0.0015805 | 11.5817 | 25.6444 |  |  |  |  | 0.44886 | 0.449 | 41 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12703 | 0.0016237 | 11.6527 | 25.6444 |  |  |  |  | 0.45163 | 0.452 | 41.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12753 | 0.001667 | 11.7238 | 25.6444 |  |  |  |  | 0.45439 | 0.454 | 41.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12802 | 0.0017104 | 11.7949 | 25.6444 |  |  |  |  | 0.45717 | 0.457 | 41.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12852 | 0.0017538 | 11.8661 | 25.6444 |  |  |  |  | 0.45994 | 0.46 | 41.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12902 | 0.0017974 | 11.9374 | 25.6444 |  |  |  |  | 0.46272 | 0.463 | 41.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.12952 | 0.001841 | 12.0088 | 25.6444 |  |  |  |  | 0.4655 | 0.465 | 41.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13002 | 0.0018847 | 12.0803 | 25.6444 |  |  |  |  | 0.46828 | 0.468 | 41.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13052 | 0.0019284 | 12.1519 | 25.6444 |  |  |  |  | 0.47107 | 0.471 | 41.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13102 | 0.0019723 | 12.2236 | 25.6444 |  |  |  |  | 0.47386 | 0.474 | 41.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13153 | 0.0020162 | 12.2953 | 25.6444 |  |  |  |  | 0.47666 | 0.477 | 42 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13204 | 0.0020603 | 12.3672 | 25.6444 |  |  |  |  | 0.47945 | 0.479 | 42.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13255 | 0.0021044 | 12.4391 | 25.6444 |  |  |  |  | 0.48225 | 0.482 | 42.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13306 | 0.0021485 | 12.5111 | 25.6444 |  |  |  |  | 0.48506 | 0.485 | 42.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13357 | 0.0021928 | 12.5832 | 25.6444 |  |  |  |  | 0.48787 | 0.488 | 42.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13409 | 0.0022372 | 12.6554 | 25.6444 |  |  |  |  | 0.49068 | 0.491 | 42.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13461 | 0.0022816 | 12.7277 | 25.6444 |  |  |  |  | 0.4935 | 0.493 | 42.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13513 | 0.0023261 | 12.8001 | 25.6444 |  |  |  |  | 0.49631 | 0.496 | 42.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13565 | 0.0023707 | 12.8726 | 25.6444 |  |  |  |  | 0.49914 | 0.499 | 42.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13617 | 0.0024154 | 12.9451 | 25.6444 |  |  |  |  | 0.50196 | 0.502 | 42.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13669 | 0.0024602 | 13.0178 | 25.6444 |  |  |  |  | 0.50479 | 0.505 | 43 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13722 | 0.002505 | 13.0905 | 25.6444 |  |  |  |  | 0.50763 | 0.508 | 43.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13775 | 0.0025499 | 13.1634 | 25.6444 |  |  |  |  | 0.51046 | 0.51 | 43.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13827 | 0.002595 | 13.2363 | 25.6444 |  |  |  |  | 0.5133 | 0.513 | 43.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13881 | 0.0026401 | 13.3093 | 25.6444 |  |  |  |  | 0.51615 | 0.516 | 43.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13934 | 0.0026852 | 13.3824 | 25.6444 |  |  |  |  | 0.51899 | 0.519 | 43.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.13987 | 0.0027305 | 13.4556 | 25.6444 |  |  |  |  | 0.52184 | 0.522 | 43.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14041 | 0.0027759 | 13.5289 | 25.6444 |  |  |  |  | 0.5247 | 0.525 | 43.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14095 | 0.0028213 | 13.6023 | 25.6444 |  |  |  |  | 0.52756 | 0.528 | 43.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14149 | 0.0028669 | 13.6758 | 25.6444 |  |  |  |  | 0.53042 | 0.53 | 43.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14203 | 0.0029125 | 13.7494 | 25.6444 |  |  |  |  | 0.53329 | 0.533 | 44 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14257 | 0.0029582 | 13.8231 | 25.6444 |  |  |  |  | 0.53615 | 0.536 | 44.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14312 | 0.003004 | 13.8968 | 25.6444 |  |  |  |  | 0.53903 | 0.539 | 44.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14367 | 0.0030499 | 13.9707 | 25.6444 |  |  |  |  | 0.5419 | 0.542 | 44.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14422 | 0.0030958 | 14.0446 | 25.6444 |  |  |  |  | 0.54478 | 0.545 | 44.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14477 | 0.0031419 | 14.1187 | 25.6444 |  |  |  |  | 0.54767 | 0.548 | 44.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14532 | 0.003188 | 14.1928 | 25.6444 |  |  |  |  | 0.55056 | 0.551 | 44.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14588 | 0.0032343 | 14.2671 | 25.6444 |  |  |  |  | 0.55345 | 0.553 | 44.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14643 | 0.0032806 | 14.3414 | 25.6444 |  |  |  |  | 0.55634 | 0.556 | 44.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14699 | 0.003327 | 14.4159 | 25.6444 |  |  |  |  | 0.55924 | 0.559 | 44.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14755 | 0.0033735 | 14.4904 | 25.6444 |  |  |  |  | 0.56214 | 0.562 | 45 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14812 | 0.0034201 | 14.565 | 25.6444 |  |  |  |  | 0.56505 | 0.565 | 45.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14868 | 0.0034667 | 14.6398 | 25.6444 |  |  |  |  | 0.56796 | 0.568 | 45.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14925 | 0.0035135 | 14.7146 | 25.6444 |  |  |  |  | 0.57087 | 0.571 | 45.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.14981 | 0.0035604 | 14.7895 | 25.6444 |  |  |  |  | 0.57379 | 0.574 | 45.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15038 | 0.0036073 | 14.8645 | 25.6444 |  |  |  |  | 0.57671 | 0.577 | 45.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15096 | 0.0036543 | 14.9397 | 25.6444 |  |  |  |  | 0.57964 | 0.58 | 45.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15153 | 0.0037015 | 15.0149 | 25.6444 |  |  |  |  | 0.58257 | 0.583 | 45.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15211 | 0.0037487 | 15.0902 | 25.6444 |  |  |  |  | 0.5855 | 0.586 | 45.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15268 | 0.003796 | 15.1656 | 25.6444 |  |  |  |  | 0.58844 | 0.588 | 45.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15326 | 0.0038434 | 15.2411 | 25.6444 |  |  |  |  | 0.59138 | 0.591 | 46 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15385 | 0.0038909 | 15.3168 | 25.6444 |  |  |  |  | 0.59433 | 0.594 | 46.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15443 | 0.0039385 | 15.3925 | 25.6444 |  |  |  |  | 0.59727 | 0.597 | 46.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15501 | 0.0039862 | 15.4683 | 25.6444 |  |  |  |  | 0.60023 | 0.6 | 46.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1556 | 0.0040339 | 15.5442 | 25.6444 |  |  |  |  | 0.60318 | 0.603 | 46.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15619 | 0.0040818 | 15.6202 | 25.6444 |  |  |  |  | 0.60614 | 0.606 | 46.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15678 | 0.0041298 | 15.6964 | 25.6444 |  |  |  |  | 0.60911 | 0.609 | 46.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15738 | 0.0041778 | 15.7726 | 25.6444 |  |  |  |  | 0.61208 | 0.612 | 46.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15797 | 0.004226 | 15.8489 | 25.6444 |  |  |  |  | 0.61505 | 0.615 | 46.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15857 | 0.0042742 | 15.9253 | 25.6444 |  |  |  |  | 0.61802 | 0.618 | 46.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15917 | 0.0043225 | 16.0019 | 25.6444 |  |  |  |  | 0.62101 | 0.621 | 47 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.15977 | 0.004371 | 16.0785 | 25.6444 |  |  |  |  | 0.62399 | 0.624 | 47.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16037 | 0.0044195 | 16.1552 | 25.6444 |  |  |  |  | 0.62698 | 0.627 | 47.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16098 | 0.0044681 | 16.2321 | 25.6444 |  |  |  |  | 0.62997 | 0.63 | 47.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16159 | 0.0045168 | 16.309 | 25.6444 |  |  |  |  | 0.63297 | 0.633 | 47.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1622 | 0.0045656 | 16.3861 | 25.6444 |  |  |  |  | 0.63597 | 0.636 | 47.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16281 | 0.0046145 | 16.4632 | 25.6444 |  |  |  |  | 0.63897 | 0.639 | 47.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16342 | 0.0046635 | 16.5405 | 25.6444 |  |  |  |  | 0.64198 | 0.642 | 47.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16404 | 0.0047126 | 16.6179 | 25.6444 |  |  |  |  | 0.64499 | 0.645 | 47.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16465 | 0.0047618 | 16.6953 | 25.6444 |  |  |  |  | 0.64801 | 0.648 | 47.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16527 | 0.0048111 | 16.7729 | 25.6444 |  |  |  |  | 0.65103 | 0.651 | 48 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1659 | 0.0048605 | 16.8506 | 25.6444 |  |  |  |  | 0.65406 | 0.654 | 48.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16652 | 0.00491 | 16.9284 | 25.6444 |  |  |  |  | 0.65708 | 0.657 | 48.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16714 | 0.0049596 | 17.0063 | 25.6444 |  |  |  |  | 0.66012 | 0.66 | 48.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16777 | 0.0050093 | 17.0843 | 25.6444 |  |  |  |  | 0.66316 | 0.663 | 48.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1684 | 0.0050591 | 17.1624 | 25.6444 |  |  |  |  | 0.6662 | 0.666 | 48.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16903 | 0.0051089 | 17.2406 | 25.6444 |  |  |  |  | 0.66924 | 0.669 | 48.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.16967 | 0.0051589 | 17.3189 | 25.6444 |  |  |  |  | 0.67229 | 0.672 | 48.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17031 | 0.005209 | 17.3973 | 25.6444 |  |  |  |  | 0.67535 | 0.675 | 48.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17094 | 0.0052592 | 17.4759 | 25.6444 |  |  |  |  | 0.67841 | 0.678 | 48.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17158 | 0.0053095 | 17.5545 | 25.6444 |  |  |  |  | 0.68147 | 0.681 | 49 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17223 | 0.0053599 | 17.6333 | 25.6444 |  |  |  |  | 0.68454 | 0.685 | 49.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17287 | 0.0054103 | 17.7122 | 25.6444 |  |  |  |  | 0.68761 | 0.688 | 49.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17352 | 0.0054609 | 17.7911 | 25.6444 |  |  |  |  | 0.69068 | 0.691 | 49.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17417 | 0.0055116 | 17.8702 | 25.6444 |  |  |  |  | 0.69376 | 0.694 | 49.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17482 | 0.0055624 | 17.9494 | 25.6444 |  |  |  |  | 0.69685 | 0.697 | 49.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17547 | 0.0056133 | 18.0287 | 25.6444 |  |  |  |  | 0.69993 | 0.7 | 49.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17613 | 0.0056643 | 18.1081 | 25.6444 |  |  |  |  | 0.70303 | 0.703 | 49.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17678 | 0.0057154 | 18.1877 | 25.6444 |  |  |  |  | 0.70612 | 0.706 | 49.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17744 | 0.0057666 | 18.2673 | 25.6444 |  |  |  |  | 0.70922 | 0.709 | 49.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17811 | 0.0058179 | 18.3471 | 25.6444 |  |  |  |  | 0.71233 | 0.712 | 50 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17877 | 0.0058693 | 18.4269 | 25.6444 |  |  |  |  | 0.71544 | 0.715 | 50.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.17944 | 0.0059208 | 18.5069 | 25.6444 |  |  |  |  | 0.71856 | 0.719 | 50.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1801 | 0.0059724 | 18.587 | 25.6444 |  |  |  |  | 0.72167 | 0.722 | 50.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18077 | 0.0060241 | 18.6672 | 25.6444 |  |  |  |  | 0.7248 | 0.725 | 50.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18145 | 0.006076 | 18.7476 | 25.6444 |  |  |  |  | 0.72792 | 0.728 | 50.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18212 | 0.0061279 | 18.828 | 25.6444 |  |  |  |  | 0.73106 | 0.731 | 50.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1828 | 0.0061799 | 18.9085 | 25.6444 |  |  |  |  | 0.73419 | 0.734 | 50.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18348 | 0.0062321 | 18.9892 | 25.6444 |  |  |  |  | 0.73733 | 0.737 | 50.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18416 | 0.0062843 | 19.07 | 25.6444 |  |  |  |  | 0.74048 | 0.74 | 50.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18484 | 0.0063366 | 19.1509 | 25.6444 |  |  |  |  | 0.74363 | 0.744 | 51 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18553 | 0.0063891 | 19.2319 | 25.6444 |  |  |  |  | 0.74678 | 0.747 | 51.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18622 | 0.0064417 | 19.313 | 25.6444 |  |  |  |  | 0.74994 | 0.75 | 51.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18691 | 0.0064943 | 19.3943 | 25.6444 |  |  |  |  | 0.75311 | 0.753 | 51.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1876 | 0.0065471 | 19.4756 | 25.6444 |  |  |  |  | 0.75628 | 0.756 | 51.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1883 | 0.0066 | 19.5571 | 25.6444 |  |  |  |  | 0.75945 | 0.759 | 51.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.189 | 0.006653 | 19.6387 | 25.6444 |  |  |  |  | 0.76263 | 0.763 | 51.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.18969 | 0.0067061 | 19.7204 | 25.6444 |  |  |  |  | 0.76581 | 0.766 | 51.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1904 | 0.0067593 | 19.8022 | 25.6444 |  |  |  |  | 0.76899 | 0.769 | 51.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.1911 | 0.0068126 | 19.8842 | 25.6444 |  |  |  |  | 0.77218 | 0.772 | 51.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19181 | 0.0068661 | 19.9663 | 25.6444 |  |  |  |  | 0.77538 | 0.775 | 52 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19252 | 0.0069196 | 20.0485 | 25.6444 |  |  |  |  | 0.77858 | 0.779 | 52.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19323 | 0.0069732 | 20.1308 | 25.6444 |  |  |  |  | 0.78179 | 0.782 | 52.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19394 | 0.007027 | 20.2132 | 25.6444 |  |  |  |  | 0.785 | 0.785 | 52.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19466 | 0.0070809 | 20.2957 | 25.6444 |  |  |  |  | 0.78821 | 0.788 | 52.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19537 | 0.0071349 | 20.3784 | 25.6444 |  |  |  |  | 0.79143 | 0.791 | 52.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19609 | 0.007189 | 20.4612 | 25.6444 |  |  |  |  | 0.79465 | 0.795 | 52.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19682 | 0.0072432 | 20.5441 | 25.6444 |  |  |  |  | 0.79788 | 0.798 | 52.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19754 | 0.0072975 | 20.6271 | 25.6444 |  |  |  |  | 0.80111 | 0.801 | 52.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19827 | 0.0073519 | 20.7103 | 25.6444 |  |  |  |  | 0.80435 | 0.804 | 52.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.199 | 0.0074064 | 20.7936 | 25.6444 |  |  |  |  | 0.80759 | 0.808 | 53 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.19973 | 0.0074611 | 20.877 | 25.6444 |  |  |  |  | 0.81084 | 0.811 | 53.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20047 | 0.0075159 | 20.9605 | 25.6444 |  |  |  |  | 0.81409 | 0.814 | 53.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2012 | 0.0075708 | 21.0442 | 25.6444 |  |  |  |  | 0.81735 | 0.817 | 53.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20194 | 0.0076258 | 21.1279 | 25.6444 |  |  |  |  | 0.82061 | 0.821 | 53.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20268 | 0.0076809 | 21.2118 | 25.6444 |  |  |  |  | 0.82388 | 0.824 | 53.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20343 | 0.0077361 | 21.2958 | 25.6444 |  |  |  |  | 0.82715 | 0.827 | 53.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20418 | 0.0077914 | 21.38 | 25.6444 |  |  |  |  | 0.83043 | 0.83 | 53.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20492 | 0.0078469 | 21.4643 | 25.6444 |  |  |  |  | 0.83371 | 0.834 | 53.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20568 | 0.0079025 | 21.5487 | 25.6444 |  |  |  |  | 0.83699 | 0.837 | 53.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20643 | 0.0079581 | 21.6332 | 25.6444 |  |  |  |  | 0.84029 | 0.84 | 54 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20719 | 0.0080139 | 21.7178 | 25.6444 |  |  |  |  | 0.84358 | 0.844 | 54.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20794 | 0.0080699 | 21.8026 | 25.6444 |  |  |  |  | 0.84688 | 0.847 | 54.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2087 | 0.0081259 | 21.8875 | 25.6444 |  |  |  |  | 0.85019 | 0.85 | 54.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.20947 | 0.0081821 | 21.9725 | 25.6444 |  |  |  |  | 0.8535 | 0.853 | 54.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21023 | 0.0082383 | 22.0577 | 25.6444 |  |  |  |  | 0.85681 | 0.857 | 54.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.211 | 0.0082947 | 22.143 | 25.6444 |  |  |  |  | 0.86014 | 0.86 | 54.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21177 | 0.0083512 | 22.2284 | 25.6444 |  |  |  |  | 0.86346 | 0.863 | 54.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21255 | 0.0084079 | 22.3139 | 25.6444 |  |  |  |  | 0.86679 | 0.867 | 54.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21332 | 0.0084646 | 22.3996 | 25.6444 |  |  |  |  | 0.87013 | 0.87 | 54.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2141 | 0.0085215 | 22.4854 | 25.6444 |  |  |  |  | 0.87347 | 0.873 | 55 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21488 | 0.0085784 | 22.5714 | 25.6444 |  |  |  |  | 0.87681 | 0.877 | 55.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21566 | 0.0086356 | 22.6574 | 25.6444 |  |  |  |  | 0.88017 | 0.88 | 55.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21645 | 0.0086928 | 22.7436 | 25.6444 |  |  |  |  | 0.88352 | 0.884 | 55.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21724 | 0.0087501 | 22.8299 | 25.6444 |  |  |  |  | 0.88688 | 0.887 | 55.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21803 | 0.0088076 | 22.9164 | 25.6444 |  |  |  |  | 0.89025 | 0.89 | 55.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21882 | 0.0088652 | 23.003 | 25.6444 |  |  |  |  | 0.89362 | 0.894 | 55.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.21962 | 0.0089229 | 23.0897 | 25.6444 |  |  |  |  | 0.897 | 0.897 | 55.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22042 | 0.0089807 | 23.1766 | 25.6444 |  |  |  |  | 0.90038 | 0.9 | 55.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22122 | 0.0090387 | 23.2636 | 25.6444 |  |  |  |  | 0.90377 | 0.904 | 55.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22202 | 0.0090968 | 23.3507 | 25.6444 |  |  |  |  | 0.90716 | 0.907 | 56 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22283 | 0.009155 | 23.4379 | 25.6444 |  |  |  |  | 0.91055 | 0.911 | 56.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22364 | 0.0092133 | 23.5253 | 25.6444 |  |  |  |  | 0.91396 | 0.914 | 56.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22445 | 0.0092717 | 23.6129 | 25.6444 |  |  |  |  | 0.91737 | 0.917 | 56.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22526 | 0.0093303 | 23.7005 | 25.6444 |  |  |  |  | 0.92078 | 0.921 | 56.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22608 | 0.009389 | 23.7883 | 25.6444 |  |  |  |  | 0.9242 | 0.924 | 56.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2269 | 0.0094478 | 23.8762 | 25.6444 |  |  |  |  | 0.92762 | 0.928 | 56.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22772 | 0.0095068 | 23.9643 | 25.6444 |  |  |  |  | 0.93105 | 0.931 | 56.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22854 | 0.0095659 | 24.0525 | 25.6444 |  |  |  |  | 0.93448 | 0.934 | 56.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.22937 | 0.0096251 | 24.1409 | 25.6444 |  |  |  |  | 0.93792 | 0.938 | 56.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2302 | 0.0096844 | 24.2293 | 25.6444 |  |  |  |  | 0.94137 | 0.941 | 57 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23103 | 0.0097439 | 24.318 | 25.6444 |  |  |  |  | 0.94482 | 0.945 | 57.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23187 | 0.0098034 | 24.4067 | 25.6444 |  |  |  |  | 0.94827 | 0.948 | 57.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2327 | 0.0098632 | 24.4956 | 25.6444 |  |  |  |  | 0.95174 | 0.952 | 57.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23354 | 0.009923 | 24.5847 | 25.6444 |  |  |  |  | 0.9552 | 0.955 | 57.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23439 | 0.009983 | 24.6738 | 25.6444 |  |  |  |  | 0.95867 | 0.959 | 57.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23523 | 0.010043 | 24.7631 | 25.6444 |  |  |  |  | 0.96215 | 0.962 | 57.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23608 | 0.010103 | 24.8526 | 25.6444 |  |  |  |  | 0.96563 | 0.966 | 57.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23693 | 0.010164 | 24.9422 | 25.6444 |  |  |  |  | 0.96912 | 0.969 | 57.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23779 | 0.010224 | 25.0319 | 25.6444 |  |  |  |  | 0.97262 | 0.973 | 57.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.23864 | 0.010285 | 25.1218 | 25.6444 |  |  |  |  | 0.97612 | 0.976 | 58 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2395 | 0.010345 | 25.2118 | 25.6444 |  |  |  |  | 0.97962 | 0.98 | 58.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24036 | 0.010406 | 25.302 | 25.6444 |  |  |  |  | 0.98313 | 0.983 | 58.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24123 | 0.010467 | 25.3923 | 25.6444 |  |  |  |  | 0.98665 | 0.987 | 58.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24209 | 0.010529 | 25.4828 | 25.6444 |  |  |  |  | 0.99017 | 0.99 | 58.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24296 | 0.01059 | 25.5733 | 25.6444 |  |  |  |  | 0.99369 | 0.994 | 58.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24384 | 0.010651 | 25.6641 | 25.6444 |  |  |  |  | 0.99723 | 0.997 | 58.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24471 | 0.010713 | 25.755 | 25.6444 |  |  |  |  | 1.0008 | 1.001 | 58.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24559 | 0.010774 | 25.846 | 25.6444 |  |  |  |  | 1.0043 | 1.004 | 58.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24647 | 0.010836 | 25.9372 | 25.6444 |  |  |  |  | 1.0079 | 1.008 | 58.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24735 | 0.010898 | 26.0285 | 25.6444 |  |  |  |  | 1.0114 | 1.011 | 59 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24824 | 0.01096 | 26.1199 | 25.6444 |  |  |  |  | 1.015 | 1.015 | 59.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.24913 | 0.011022 | 26.2116 | 25.6444 |  |  |  |  | 1.0185 | 1.019 | 59.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25002 | 0.011085 | 26.3033 | 25.6444 |  |  |  |  | 1.0221 | 1.022 | 59.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25092 | 0.011147 | 26.3952 | 25.6444 |  |  |  |  | 1.0257 | 1.026 | 59.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25181 | 0.01121 | 26.4873 | 25.6444 |  |  |  |  | 1.0293 | 1.029 | 59.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25271 | 0.011273 | 26.5795 | 25.6444 |  |  |  |  | 1.0329 | 1.033 | 59.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25362 | 0.011336 | 26.6718 | 25.6444 |  |  |  |  | 1.0365 | 1.036 | 59.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25452 | 0.011399 | 26.7643 | 25.6444 |  |  |  |  | 1.0401 | 1.04 | 59.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25543 | 0.011462 | 26.857 | 25.6444 |  |  |  |  | 1.0437 | 1.044 | 59.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25634 | 0.011525 | 26.9498 | 25.6444 |  |  |  |  | 1.0473 | 1.047 | 60 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25726 | 0.011588 | 27.0427 | 25.6444 |  |  |  |  | 1.0509 | 1.051 | 60.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.25818 | 0.011652 | 27.1358 | 25.6444 |  |  |  |  | 1.0545 | 1.055 | 60.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2591 | 0.011716 | 27.2291 | 25.6444 |  |  |  |  | 1.0582 | 1.058 | 60.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26002 | 0.01178 | 27.3225 | 25.6444 |  |  |  |  | 1.0618 | 1.062 | 60.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26095 | 0.011844 | 27.416 | 25.6444 |  |  |  |  | 1.0654 | 1.065 | 60.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26188 | 0.011908 | 27.5098 | 25.6444 |  |  |  |  | 1.0691 | 1.069 | 60.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26281 | 0.011972 | 27.6036 | 25.6444 |  |  |  |  | 1.0727 | 1.073 | 60.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26374 | 0.012036 | 27.6976 | 25.6444 |  |  |  |  | 1.0764 | 1.076 | 60.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26468 | 0.012101 | 27.7918 | 25.6444 |  |  |  |  | 1.0801 | 1.08 | 60.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26562 | 0.012166 | 27.8861 | 25.6444 |  |  |  |  | 1.0837 | 1.084 | 61 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26656 | 0.012231 | 27.9806 | 25.6444 |  |  |  |  | 1.0874 | 1.087 | 61.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26751 | 0.012296 | 28.0752 | 25.6444 |  |  |  |  | 1.0911 | 1.091 | 61.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26846 | 0.012361 | 28.17 | 25.6444 |  |  |  |  | 1.0948 | 1.095 | 61.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.26941 | 0.012426 | 28.265 | 25.6444 |  |  |  |  | 1.0985 | 1.098 | 61.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27037 | 0.012491 | 28.3601 | 25.6444 |  |  |  |  | 1.1022 | 1.102 | 61.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27133 | 0.012557 | 28.4553 | 25.6444 |  |  |  |  | 1.1059 | 1.106 | 61.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27229 | 0.012623 | 28.5508 | 25.6444 |  |  |  |  | 1.1096 | 1.11 | 61.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27325 | 0.012689 | 28.6463 | 25.6444 |  |  |  |  | 1.1133 | 1.113 | 61.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27422 | 0.012755 | 28.7421 | 25.6444 |  |  |  |  | 1.1171 | 1.117 | 61.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27519 | 0.012821 | 28.838 | 25.6444 |  |  |  |  | 1.1208 | 1.121 | 62 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27616 | 0.012887 | 28.934 | 25.6444 |  |  |  |  | 1.1245 | 1.125 | 62.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27714 | 0.012953 | 29.0302 | 25.6444 |  |  |  |  | 1.1283 | 1.128 | 62.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.27812 | 0.01302 | 29.1266 | 25.6444 |  |  |  |  | 1.132 | 1.132 | 62.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2791 | 0.013087 | 29.2232 | 25.6444 |  |  |  |  | 1.1358 | 1.136 | 62.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28009 | 0.013154 | 29.3199 | 25.6444 |  |  |  |  | 1.1396 | 1.14 | 62.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28108 | 0.013221 | 29.4167 | 25.6444 |  |  |  |  | 1.1433 | 1.143 | 62.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28207 | 0.013288 | 29.5137 | 25.6444 |  |  |  |  | 1.1471 | 1.147 | 62.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28306 | 0.013355 | 29.6109 | 25.6444 |  |  |  |  | 1.1509 | 1.151 | 62.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28406 | 0.013423 | 29.7083 | 25.6444 |  |  |  |  | 1.1547 | 1.155 | 62.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28506 | 0.01349 | 29.8058 | 25.6444 |  |  |  |  | 1.1585 | 1.158 | 63 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28606 | 0.013558 | 29.9034 | 25.6444 |  |  |  |  | 1.1623 | 1.162 | 63.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28707 | 0.013626 | 30.0013 | 25.6444 |  |  |  |  | 1.1661 | 1.166 | 63.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28808 | 0.013694 | 30.0993 | 25.6444 |  |  |  |  | 1.1699 | 1.17 | 63.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.28909 | 0.013762 | 30.1975 | 25.6444 |  |  |  |  | 1.1737 | 1.174 | 63.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29011 | 0.013831 | 30.2958 | 25.6444 |  |  |  |  | 1.1775 | 1.178 | 63.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29113 | 0.013899 | 30.3943 | 25.6444 |  |  |  |  | 1.1814 | 1.181 | 63.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29215 | 0.013968 | 30.493 | 25.6444 |  |  |  |  | 1.1852 | 1.185 | 63.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29318 | 0.014037 | 30.5918 | 25.6444 |  |  |  |  | 1.1891 | 1.189 | 63.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29421 | 0.014106 | 30.6908 | 25.6444 |  |  |  |  | 1.1929 | 1.193 | 63.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29524 | 0.014175 | 30.79 | 25.6444 |  |  |  |  | 1.1968 | 1.197 | 64 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29628 | 0.014244 | 30.8893 | 25.6444 |  |  |  |  | 1.2006 | 1.201 | 64.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29731 | 0.014314 | 30.9888 | 25.6444 |  |  |  |  | 1.2045 | 1.205 | 64.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.29836 | 0.014384 | 31.0885 | 25.6444 |  |  |  |  | 1.2084 | 1.208 | 64.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.2994 | 0.014453 | 31.1884 | 25.6444 |  |  |  |  | 1.2123 | 1.212 | 64.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30045 | 0.014523 | 31.2884 | 25.6444 |  |  |  |  | 1.2162 | 1.216 | 64.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.3015 | 0.014593 | 31.3886 | 25.6444 |  |  |  |  | 1.2201 | 1.22 | 64.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30255 | 0.014664 | 31.489 | 25.6444 |  |  |  |  | 1.224 | 1.224 | 64.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30361 | 0.014734 | 31.5895 | 25.6444 |  |  |  |  | 1.2279 | 1.228 | 64.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30467 | 0.014805 | 31.6902 | 25.6444 |  |  |  |  | 1.2318 | 1.232 | 64.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30574 | 0.014875 | 31.7911 | 25.6444 |  |  |  |  | 1.2358 | 1.236 | 65 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.3068 | 0.014946 | 31.8922 | 25.6444 |  |  |  |  | 1.2397 | 1.24 | 65.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30787 | 0.015017 | 31.9934 | 25.6444 |  |  |  |  | 1.2436 | 1.244 | 65.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.30895 | 0.015089 | 32.0948 | 25.6444 |  |  |  |  | 1.2476 | 1.248 | 65.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31003 | 0.01516 | 32.1964 | 25.6444 |  |  |  |  | 1.2515 | 1.252 | 65.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31111 | 0.015232 | 32.2981 | 25.6444 |  |  |  |  | 1.2555 | 1.255 | 65.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31219 | 0.015303 | 32.4001 | 25.6444 |  |  |  |  | 1.2595 | 1.259 | 65.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31328 | 0.015375 | 32.5022 | 25.6444 |  |  |  |  | 1.2634 | 1.263 | 65.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31437 | 0.015447 | 32.6045 | 25.6444 |  |  |  |  | 1.2674 | 1.267 | 65.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31546 | 0.015519 | 32.707 | 25.6444 |  |  |  |  | 1.2714 | 1.271 | 65.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31656 | 0.015592 | 32.8096 | 25.6444 |  |  |  |  | 1.2754 | 1.275 | 66 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31766 | 0.015664 | 32.9124 | 25.6444 |  |  |  |  | 1.2794 | 1.279 | 66.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31876 | 0.015737 | 33.0154 | 25.6444 |  |  |  |  | 1.2834 | 1.283 | 66.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.31987 | 0.01581 | 33.1186 | 25.6444 |  |  |  |  | 1.2874 | 1.287 | 66.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32098 | 0.015883 | 33.222 | 25.6444 |  |  |  |  | 1.2915 | 1.291 | 66.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32209 | 0.015956 | 33.3255 | 25.6444 |  |  |  |  | 1.2955 | 1.295 | 66.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32321 | 0.016029 | 33.4293 | 25.6444 |  |  |  |  | 1.2995 | 1.3 | 66.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32433 | 0.016103 | 33.5332 | 25.6444 |  |  |  |  | 1.3036 | 1.304 | 66.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32546 | 0.016177 | 33.6373 | 25.6444 |  |  |  |  | 1.3076 | 1.308 | 66.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32658 | 0.01625 | 33.7416 | 25.6444 |  |  |  |  | 1.3117 | 1.312 | 66.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32772 | 0.016324 | 33.846 | 25.6444 |  |  |  |  | 1.3157 | 1.316 | 67 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32885 | 0.016399 | 33.9507 | 25.6444 |  |  |  |  | 1.3198 | 1.32 | 67.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.32999 | 0.016473 | 34.0555 | 25.6444 |  |  |  |  | 1.3239 | 1.324 | 67.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33113 | 0.016548 | 34.1605 | 25.6444 |  |  |  |  | 1.328 | 1.328 | 67.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33227 | 0.016622 | 34.2657 | 25.6444 |  |  |  |  | 1.3321 | 1.332 | 67.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33342 | 0.016697 | 34.3711 | 25.6444 |  |  |  |  | 1.3362 | 1.336 | 67.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33457 | 0.016772 | 34.4767 | 25.6444 |  |  |  |  | 1.3403 | 1.34 | 67.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33573 | 0.016847 | 34.5824 | 25.6444 |  |  |  |  | 1.3444 | 1.344 | 67.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33689 | 0.016923 | 34.6884 | 25.6444 |  |  |  |  | 1.3485 | 1.349 | 67.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33805 | 0.016998 | 34.7945 | 25.6444 |  |  |  |  | 1.3527 | 1.353 | 67.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.33921 | 0.017074 | 34.9008 | 25.6444 |  |  |  |  | 1.3568 | 1.357 | 68 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34038 | 0.01715 | 35.0074 | 25.6444 |  |  |  |  | 1.361 | 1.361 | 68.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34156 | 0.017226 | 35.1141 | 25.6444 |  |  |  |  | 1.3651 | 1.365 | 68.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34273 | 0.017303 | 35.221 | 25.6444 |  |  |  |  | 1.3693 | 1.369 | 68.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34391 | 0.017379 | 35.3281 | 25.6444 |  |  |  |  | 1.3734 | 1.373 | 68.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.3451 | 0.017456 | 35.4353 | 25.6444 |  |  |  |  | 1.3776 | 1.378 | 68.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34628 | 0.017532 | 35.5428 | 25.6444 |  |  |  |  | 1.3818 | 1.382 | 68.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34747 | 0.017609 | 35.6505 | 25.6444 |  |  |  |  | 1.386 | 1.386 | 68.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34867 | 0.017687 | 35.7583 | 25.6444 |  |  |  |  | 1.3902 | 1.39 | 68.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.34986 | 0.017764 | 35.8664 | 25.6444 |  |  |  |  | 1.3944 | 1.394 | 68.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35107 | 0.017841 | 35.9746 | 25.6444 |  |  |  |  | 1.3986 | 1.399 | 69 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35227 | 0.017919 | 36.0831 | 25.6444 |  |  |  |  | 1.4028 | 1.403 | 69.1 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35348 | 0.017997 | 36.1917 | 25.6444 |  |  |  |  | 1.4071 | 1.407 | 69.2 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35469 | 0.018075 | 36.3006 | 25.6444 |  |  |  |  | 1.4113 | 1.411 | 69.3 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35591 | 0.018153 | 36.4096 | 25.6444 |  |  |  |  | 1.4155 | 1.416 | 69.4 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35713 | 0.018232 | 36.5188 | 25.6444 |  |  |  |  | 1.4198 | 1.42 | 69.5 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35835 | 0.01831 | 36.6282 | 25.6444 |  |  |  |  | 1.424 | 1.424 | 69.6 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.35958 | 0.018389 | 36.7379 | 25.6444 |  |  |  |  | 1.4283 | 1.428 | 69.7 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.36081 | 0.018468 | 36.8477 | 25.6444 |  |  |  |  | 1.4326 | 1.433 | 69.8 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.36204 | 0.018547 | 36.9577 | 25.6444 |  |  |  |  | 1.4369 | 1.437 | 69.9 | 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546
[9 empty] | 58.1856 | 0.36328 | C15: 1.4412; C16: 1.441; C17: 70; C18: 14.6958 | -10440.397 | -11.2947 | -0.027022 | 1.289e-05 | -2.4781e-09 | 6.546